## raw_OpenNEM_data
date | Pumps - MW | Exports - MW | Imports - MW | Coal (Black) - MW | Distillate - MW | Gas (CCGT) - MW | Gas (OCGT) - MW | Hydro - MW | Wind - MW | Solar (Utility) - MW | Solar (Rooftop) - MW | Temperature - C | Emissions Intensity - kgCO₂e/MWh | Price - AUD/MWh
2020-12-26 17:30 | 0 | -278.5 | 0 | 6042.36 | -0.01 | 0.11 | 0 | 131.9 | 470.42 | 726.7 | 269.63 | 20.9 | NaN | 40.82
2020-12-26 18:00 | 0 | -376.01 | 0 | 6360.28 | -0.01 | 0.12 | 0 | 151.95 | 548.93 | 508.37 | 137.31 | 20.83 | NaN | 47.77
2020-12-26 18:30 | 0 | -491.17 | 0 | 6484.08 | 0 | 0.11 | 0 | 330.62 | 657.43 | 296.59 | 47.42 | 20.73 | NaN | 38.9
2020-12-26 19:00 | 0 | -400.47 | 0 | 6577.95 | 0 | 0.14 | 0 | 332.54 | 729 | 81.69 | 8.59 | 19.39 | NaN | 46.08
2020-12-26 19:30 | 0 | -402.03 | 0 | 6641.53 | 0 | 0.15 | 0 | 314.98 | 773.24 | 3.23 | 0.57 | 18.99 | NaN | 46.46
2020-12-26 20:00 | 0 | -381.63 | 0 | 6641.97 | 0 | 0.15 | 0 | 252.03 | 758.55 | -0.54 | 0 | 18.76 | NaN | 47.4
2020-12-26 20:30 | 0 | -355.36 | 0 | 6570.64 | 0 | 0.15 | 0 | 222.78 | 734.57 | -0.55 | 0 | 18.78 | NaN | 42.03
2020-12-26 21:00 | 0 | -310.92 | 0 | 6505.18 | 0 | 0.15 | 0 | 120.71 | 738.54 | -0.55 | 0 | 18.8 | NaN | 39.65
2020-12-26 21:30 | 0 | -239.43 | 0 | 6406.43 | 0 | 0.14 | 0 | 100.33 | 715.37 | -0.56 | 0 | 18.8 | NaN | 39.29
2020-12-26 22:00 | 0 | -61.61 | 1.94 | 6212.06 | -0.01 | 0.14 | 0 | 100.5 | 679.52 | -0.51 | 0 | 18.81 | NaN | 35.47
2020-12-26 22:30 | 0 | -98.69 | 0 | 6183.96 | -0.01 | 0.15 | 0 | 100.48 | 665.62 | -0.54 | 0 | 18.86 | NaN | 42.52
2020-12-26 23:00 | 0 | -16.11 | 56.48 | 5940.64 | -0.02 | 0.14 | 0 | 100.6 | 660.58 | -0.51 | 0 | 18.67 | NaN | 35.94
2020-12-26 23:30 | 0 | 0 | 151.31 | 5685.4 | -0.03 | 0.15 | 0 | 100.39 | 622.28 | -0.41 | 0 | 18.77 | NaN | 38.82
2020-12-27 | 0 | 0 | 434.88 | 5409.52 | -0.03 | 0.15 | 0 | 100.63 | 581.53 | -0.44 | 0 | 18.78 | NaN | 39.84
2020-12-27 00:30 | 0 | 0 | 700.03 | 4939.09 | -0.03 | 0.14 | 0 | 100.55 | 548.57 | -0.51 | 0 | 18.6 | NaN | 36.83
2020-12-27 01:00 | 0 | 0 | 655.24 | 4787.44 | -0.03 | 0.14 | 0 | 100.71 | 538.68 | -0.45 | 0 | 18.27 | NaN | 39.83
2020-12-27 01:30 | 0 | 0 | 712.78 | 4560.5 | -0.03 | 0.14 | 0 | 100.56 | 500.49 | -0.49 | 0 | 18.18 | NaN | 34.76
2020-12-27 02:00 | 0 | 0 | 969.68 | 4184.95 | -0.02 | 0.14 | 0 | 100.48 | 446.2 | -0.55 | 0 | 18.02 | NaN | 32.45
2020-12-27 02:30 | 0 | 0 | 1033.92 | 4033.11 | -0.03 | 0.13 | 0 | 100.58 | 393.81 | -0.56 | 0 | 17.83 | NaN | 28.26
2020-12-27 03:00 | 0 | 0 | 1135.81 | 3976.7 | -0.03 | 0.13 | 0 | 100.07 | 358.25 | -0.48 | 0 | 17.71 | NaN | 32.56
2020-12-27 03:30 | 0 | 0 | 1137.56 | 3841.08 | -0.03 | 0.14 | 0 | 100.5 | 445.67 | -0.48 | 0 | 17.61 | NaN | 31.14
2020-12-27 04:00 | 0 | 0 | 1135.12 | 3819.61 | -0.03 | 0.14 | 0 | 100.64 | 487.01 | -0.54 | 0.17 | 17.52 | NaN | 29.19
2020-12-27 04:30 | 0 | 0 | 1211.07 | 3794.58 | -0.03 | 0.14 | 0 | 100.45 | 484.86 | -0.45 | 5.63 | 17.53 | NaN | 32.31
2020-12-27 05:00 | 0 | 0 | 1214.16 | 3808.86 | -0.03 | 0.12 | 0 | 100.82 | 467.26 | 1.07 | 50.28 | 17.77 | NaN | 33.35
2020-12-27 05:30 | 0 | 0 | 1184.04 | 3796.76 | -0.03 | 0.09 | 0 | 100.73 | 494.34 | 51.95 | 156.51 | 17.98 | NaN | 33.52
2020-12-27 06:00 | 0 | 0 | 1110.02 | 3745.5 | -0.03 | 0.13 | 0 | 100.34 | 455.47 | 255.08 | 329.42 | 18.22 | NaN | 28.91
2020-12-27 06:30 | 0 | 0 | 1096.66 | 3688.56 | -0.03 | 0.12 | 0 | 100.81 | 342.17 | 517.89 | 558.22 | 18.72 | NaN | 12.3
2020-12-27 07:00 | 0 | 0 | 1111.49 | 3603.97 | -0.03 | 0.1 | 0 | 100.15 | 274.75 | 752.31 | 839.27 | 19 | NaN | 11.33
2020-12-27 07:30 | -70.92 | 0 | 1106.31 | 3662.14 | -0.03 | 0.12 | 0 | 100.71 | 262.52 | 876.12 | 1157.8 | 19.4 | NaN | -2
2020-12-27 08:00 | -133.66 | 0 | 1107.63 | 3578.85 | -0.03 | 0.11 | 0 | 100.46 | 251.33 | 941.9 | 1454.01 | 20.17 | NaN | 0.89
2020-12-27 08:30 | -272.17 | 0 | 1025.64 | 3694.23 | -0.03 | 0.12 | 0 | 100.78 | 331.76 | 978.95 | 1689.52 | 21.26 | NaN | 15.92
2020-12-27 09:00 | -272.43 | 0 | 938.85 | 3626.49 | -0.03 | 0.1 | 0 | 101.57 | 339.03 | 1044.18 | 1899.16 | 22.13 | NaN | 15.58
2020-12-27 09:30 | -271.49 | 0 | 873.5 | 3550.11 | -0.03 | 0.13 | 0 | 101.57 | 382.22 | 1089.3 | 2078.62 | 23.68 | NaN | -0.18
2020-12-27 10:00 | -319.52 | 0 | 914.43 | 3506.11 | -0.03 | 0.13 | 0 | 100.94 | 353.04 | 1071.47 | 2232.9 | 24.77 | NaN | -2.07
2020-12-27 10:30 | -463.47 | 0 | 899.66 | 3641 | -0.03 | 0.12 | 0 | 97.57 | 399.39 | 1067.19 | 2337.22 | 26.01 | NaN | 5.82
2020-12-27 11:00 | -398.27 | 0 | 753.07 | 3719.49 | -0.03 | 0.14 | 0 | 97.45 | 362.92 | 1109.77 | 2403.11 | 26.57 | NaN | 14.39
2020-12-27 11:30 | -271.25 | 0 | 800.1 | 3727.23 | -0.02 | 0.13 | 0 | 97.06 | 322.59 | 1105.43 | 2423.53 | 26.27 | NaN | 24.21
2020-12-27 12:00 | -245.84 | 0 | 910.14 | 3677.05 | -0.02 | 0.13 | 0 | 96.73 | 311.5 | 1100.82 | 2396.54 | 26.68 | NaN | 29.09
2020-12-27 12:30 | -64.27 | 0 | 922.41 | 3719.04 | -0.02 | 0.14 | 0 | 97.38 | 366.08 | 1011.65 | 2359.91 | 25.98 | NaN | 21.97
2020-12-27 13:00 | 0 | 0 | 943 | 3833.75 | -0.02 | 0.14 | 0 | 97.39 | 377.55 | 1023.08 | 2294.11 | 25.71 | NaN | 26.57
2020-12-27 13:30 | 0 | 0 | 1069.48 | 3884.98 | -0.02 | 0.13 | 0 | 97.45 | 411.96 | 996.54 | 2154.1 | 25.61 | NaN | 31.47
2020-12-27 14:00 | 0 | 0 | 1234.91 | 3965.43 | -0.01 | 0.13 | 0 | 97.47 | 450.48 | 996.9 | 2012.86 | 25.57 | NaN | 32.83
2020-12-27 14:30 | 0 | 0 | 1397.71 | 4082.78 | 0 | 0.12 | 0 | 117.14 | 501.5 | 885.55 | 1855.1 | 26.11 | NaN | 34.87
2020-12-27 15:00 | 0 | 0 | 1542.41 | 4236.58 | 0 | 0.15 | 0 | 168.99 | 467.07 | 807.62 | 1630.28 | 26.42 | NaN | 34.84
2020-12-27 15:30 | 0 | 0 | 1443.88 | 4583.74 | 0 | 0.15 | 0 | 298.98 | 519.03 | 705.32 | 1383.58 | 26.14 | NaN | 35.7
2020-12-27 16:00 | 0 | 0 | 1245.91 | 5056.04 | 0.01 | 0.15 | 0 | 471.38 | 537.04 | 608.59 | 1083.89 | 25.83 | NaN | 39.22
2020-12-27 16:30 | 0 | 0 | 990.64 | 5662.38 | 0.01 | 0.14 | 0 | 522.87 | 555.31 | 489.46 | 740.33 | 25.57 | NaN | 38.7
2020-12-27 17:00 | 0 | 0 | 862.13 | 6268.8 | 0.01 | 0.14 | 0 | 553.31 | 565.57 | 384.88 | 476 | 24.9 | NaN | 39.38
2020-12-27 17:30 | 0 | 0 | 740.72 | 6519.62 | 0.01 | 0.14 | 0 | 579.71 | 539.06 | 239.02 | 299.17 | 24.45 | NaN | 39.38
2020-12-27 18:00 | 0 | 0 | 472.39 | 6865.81 | 0.01 | 0.14 | 0 | 647.09 | 444.82 | 193.76 | 151 | 24.22 | NaN | 40.85
2020-12-27 18:30 | 0 | 0 | 489.62 | 6942.99 | 0.02 | 0.13 | 0 | 604.08 | 412.47 | 84.94 | 49.91 | 24.03 | NaN | 39.41
2020-12-27 19:00 | 0 | 0 | 486.13 | 6941.02 | 0.02 | 0.14 | 0 | 587.27 | 420.27 | 19.62 | 7.39 | 23.92 | NaN | 40.54
2020-12-27 19:30 | 0 | 0 | 563.71 | 6863.44 | 0.02 | 0.15 | 0 | 592.69 | 400.41 | 0.12 | 0.29 | 23.91 | NaN | 41.93
2020-12-27 20:00 | 0 | 0 | 522.55 | 6851.17 | 0.01 | 0.15 | 0 | 614.34 | 299.7 | -0.46 | 0 | 23.98 | NaN | 46.79
2020-12-27 20:30 | 0 | 0 | 692.51 | 6580.7 | 0.01 | 0.15 | 0 | 505.68 | 369.91 | -0.54 | 0 | 23.91 | NaN | 41.13
2020-12-27 21:00 | 0 | 0 | 634.14 | 6222.68 | 0.01 | 0.14 | 0 | 461.69 | 590.8 | -0.51 | 0 | 23.83 | NaN | 32.47
2020-12-27 21:30 | 0 | 0 | 481.04 | 6202.19 | 0.01 | 0.16 | 0 | 397.23 | 696.52 | -0.54 | 0 | 23.98 | NaN | 38.12
2020-12-27 22:00 | 0 | 0 | 518.62 | 5972.33 | 0 | 0.16 | 0 | 373.03 | 773.82 | -0.54 | 0 | 24.09 | NaN | 34.86
2020-12-27 22:30 | 0 | 0 | 497.98 | 5807.74 | 0 | 0.15 | 0 | 329.19 | 804.47 | -0.41 | 0 | 24.17 | NaN | 39.93
2020-12-27 23:00 | 0 | 0 | 648.88 | 5380.32 | -0.01 | 0.15 | 0 | 282.43 | 868.11 | -0.32 | 0 | 24.1 | NaN | 35.8
2020-12-27 23:30 | 0 | 0 | 691.39 | 5124.3 | -0.02 | 0.16 | 0 | 216.25 | 965.32 | -0.41 | 0 | 23.94 | NaN | 39.27
2020-12-28 | 0 | 0 | 815.53 | 4824.57 | -0.02 | 0.15 | 0 | 189.25 | 1015.05 | -0.5 | 0 | 23.98 | NaN | 39.63
2020-12-28 00:30 | 0 | 0 | 948.32 | 4514.43 | -0.03 | 0.15 | 0 | 165.85 | 967.97 | -0.53 | 0 | 24.06 | NaN | 38.28
2020-12-28 01:00 | 0 | 0 | 1023.22 | 4354.43 | -0.03 | 0.15 | 0 | 97.27 | 945.18 | -0.44 | 0 | 24.63 | NaN | 38.15
2020-12-28 01:30 | 0 | 0 | 1007.93 | 4170.66 | -0.03 | 0.15 | 0 | 97.2 | 912.03 | -0.47 | 0 | 25.11 | NaN | 35.23
2020-12-28 02:00 | 0 | 0 | 986.38 | 4044.01 | -0.03 | 0.15 | 0 | 97.22 | 895.07 | -0.48 | 0 | 25.06 | NaN | 34.98
2020-12-28 02:30 | 0 | 0 | 1010.36 | 4007.53 | -0.03 | 0.15 | 0 | 97.27 | 848.84 | -0.48 | 0 | 24.48 | NaN | 35.35
2020-12-28 03:00 | 0 | 0 | 1032.49 | 3940.89 | -0.03 | 0.15 | 0 | 97.29 | 822.59 | -0.55 | 0 | 24.07 | NaN | 35.44
2020-12-28 03:30 | 0 | 0 | 1017.21 | 3945.89 | -0.03 | 0.15 | 0 | 97.33 | 836.3 | -0.51 | 0 | 24.09 | NaN | 35.8
2020-12-28 04:00 | 0 | 0 | 1053.98 | 3938.38 | -0.03 | 0.15 | 0 | 97.35 | 811.06 | -0.42 | 0.05 | 24.18 | NaN | 35.45
2020-12-28 04:30 | 0 | 0 | 1058.64 | 4059.84 | -0.03 | 0.14 | 0 | 97.4 | 748.26 | -0.48 | 2.7 | 24.23 | NaN | 39.1
2020-12-28 05:00 | 0 | 0 | 1051.96 | 4190.36 | -0.03 | 0.14 | 0 | 97.2 | 679.34 | -0.11 | 28.03 | 24.56 | NaN | 39.03
2020-12-28 05:30 | 0 | 0 | 1045.57 | 4323.23 | -0.03 | 0.13 | 0 | 97.42 | 654.93 | 13 | 91.33 | 24.86 | NaN | 40.91
2020-12-28 06:00 | 0 | 0 | 1228.49 | 4161.07 | -0.03 | 0.12 | 0 | 97.53 | 632.44 | 160.03 | 184.8 | 25.05 | NaN | 39.53
2020-12-28 06:30 | 0 | 0 | 1470.18 | 3804.34 | -0.03 | 0.14 | 0 | 97.39 | 587.2 | 388.04 | 303.9 | 25.69 | NaN | 33.39
2020-12-28 07:00 | 0 | 0 | 1268.94 | 3769.22 | -0.03 | 0.13 | 0 | 97.75 | 650.23 | 679.13 | 450.61 | 26.06 | NaN | 20.97
2020-12-28 07:30 | 0 | 0 | 1057.84 | 3842.64 | -0.03 | 0.12 | 0 | 98.08 | 762.27 | 798.63 | 689.73 | 26.22 | NaN | 20.08
2020-12-28 08:00 | 0 | 0 | 999.05 | 3854.23 | -0.03 | 0.11 | 0 | 98.14 | 800.14 | 830.29 | 1027.33 | 26.63 | NaN | 11.98
2020-12-28 08:30 | -7.16 | 0 | 1051.98 | 3796.92 | -0.03 | 0.13 | 0 | 99.34 | 768.86 | 849.98 | 1318.13 | 27.72 | NaN | 18.29
2020-12-28 09:00 | -127.98 | 0 | 1179.84 | 3788.15 | -0.03 | 0.13 | 0 | 99.28 | 727.21 | 907 | 1593.16 | 29 | NaN | 9.13
2020-12-28 09:30 | -200.66 | 0 | 1168.99 | 3854.46 | -0.04 | 0.13 | 0 | 99.28 | 703.38 | 904.52 | 1759.19 | 28.66 | NaN | 28.91
2020-12-28 10:00 | -200.57 | 0 | 1266.62 | 3837.8 | -0.03 | 0.14 | 0 | 99.6 | 750.17 | 894.75 | 1827.19 | 27.21 | NaN | 20.27
2020-12-28 10:30 | -200.05 | 0 | 1221.01 | 3869.07 | -0.03 | 0.14 | 0 | 99.58 | 772.24 | 971.1 | 1860.1 | 26.27 | NaN | 25.48
2020-12-28 11:00 | -200.75 | 0 | 1210.38 | 3866.13 | -0.03 | 0.15 | 0 | 99.54 | 777.74 | 957.32 | 1913.21 | 26.21 | NaN | 19.26
2020-12-28 11:30 | -200.31 | 0 | 1172.43 | 4001.03 | -0.04 | 0.15 | 0 | 99.5 | 738.39 | 1004.5 | 1947.85 | 25.64 | NaN | 23.4
2020-12-28 12:00 | -200.41 | 0 | 1077.9 | 4039.94 | -0.04 | 0.15 | 0 | 99.68 | 803.76 | 1006.82 | 1824.57 | 24.77 | NaN | 24.14
2020-12-28 12:30 | -200.58 | 0 | 1090.17 | 4161.44 | -0.04 | 0.15 | 0 | 99.76 | 839.77 | 980.8 | 1677.2 | 23.75 | NaN | 25.13
2020-12-28 13:00 | -200.41 | 0 | 1114.2 | 4231.83 | -0.03 | 0.14 | 0 | 99.4 | 752.21 | 983.14 | 1603.82 | 22.49 | NaN | 26.76
2020-12-28 13:30 | -200.53 | 0 | 1224.82 | 4189.5 | -0.03 | 0.13 | 0 | 99.52 | 636.46 | 984.52 | 1459.27 | 21.83 | NaN | 30.18
2020-12-28 14:00 | -200.28 | 0 | 1148.21 | 4219.28 | -0.04 | 0.15 | 0 | 99.44 | 709.42 | 1007.24 | 1238.54 | 21.29 | NaN | 25.79
2020-12-28 14:30 | -147.28 | 0 | 1180.75 | 4292.39 | -0.04 | 0.14 | 0 | 99.58 | 724.24 | 949.51 | 1048.21 | 21.09 | NaN | 32.96
2020-12-28 15:00 | -80.54 | 0 | 1032.26 | 4445.05 | -0.04 | 0.14 | 0 | 100.95 | 783.53 | 879.57 | 831.19 | 20.83 | NaN | 35.55
2020-12-28 15:30 | 0 | 0 | 918.09 | 4750.45 | -0.04 | 0.14 | 0 | 131.41 | 711.98 | 858.3 | 676.62 | 20.58 | NaN | 40.82
2020-12-28 16:00 | 0 | 0 | 555.25 | 5321.28 | -0.03 | 0.12 | 0 | 170.13 | 731.11 | 810.74 | 521.94 | 19.99 | NaN | 41.15
2020-12-28 16:30 | 0 | 0 | 252.4 | 5813.61 | -0.03 | 0.12 | 0 | 207.25 | 791.24 | 612.33 | 385.57 | 19.57 | NaN | 43.41
2020-12-28 17:00 | 0 | -6.82 | 94.06 | 6161.4 | -0.04 | 0.14 | 0 | 231.73 | 823.83 | 622.25 | 257.68 | 18.72 | NaN | 36.07
2020-12-28 17:30 | 0 | 0 | 240.22 | 6123.49 | -0.02 | 0.13 | 0 | 293.6 | 734.8 | 520.73 | 155.62 | 18.1 | NaN | 25.94
2020-12-28 18:00 | 0 | 0 | 353 | 5987.93 | -0.02 | 0.13 | 0 | 330.56 | 751.07 | 379.8 | 84.25 | 18.01 | NaN | 35.34
2020-12-28 18:30 | 0 | 0 | 416.34 | 5968.4 | -0.02 | 0.12 | 0 | 317.85 | 714.9 | 197.81 | 34.77 | 18.07 | NaN | 36.92
2020-12-28 19:00 | 0 | 0 | 404.22 | 6201.05 | -0.02 | 0.13 | 0 | 130.66 | 688.37 | 58.26 | 7.11 | 18.02 | NaN | 38.51
2020-12-28 19:30 | 0 | 0 | 363.58 | 6254.18 | -0.02 | 0.14 | 0 | 121.6 | 716.38 | 2.06 | 0.51 | 17.97 | NaN | 38.51
2020-12-28 20:00 | 0 | 0 | 302.65 | 6211.16 | -0.02 | 0.15 | 0 | 99.59 | 731.58 | -0.39 | 0 | 17.73 | NaN | 39
2020-12-28 20:30 | 0 | 0 | 370.83 | 6070.34 | -0.03 | 0.14 | 0 | 99.32 | 674.55 | -0.39 | 0 | 17.53 | NaN | 38.94
2020-12-28 21:00 | 0 | 0 | 345.54 | 6052.67 | -0.03 | 0.14 | 0 | 99.52 | 629.98 | -0.36 | 0 | 17.42 | NaN | 38.94
2020-12-28 21:30 | 0 | 0 | 305.09 | 6114.17 | -0.03 | 0.14 | 0 | 99.44 | 596.32 | -0.33 | 0 | 17.4 | NaN | 39.12
2020-12-28 22:00 | 0 | 0 | 404.19 | 5970.68 | -0.04 | 0.14 | 0 | 99.44 | 564.35 | -0.33 | 0 | 17.38 | NaN | 40.01
2020-12-28 22:30 | 0 | 0 | 272.44 | 6073.67 | -0.04 | 0.14 | 0 | 99.48 | 543.56 | -0.36 | 0 | 17.23 | NaN | 41.68
2020-12-28 23:00 | 0 | -11.26 | 101.59 | 6125.39 | -0.04 | 0.13 | 0 | 99.64 | 566.16 | -0.3 | 0 | 17.13 | NaN | 39.64
2020-12-28 23:30 | 0 | -118.62 | 0 | 6149.45 | -0.03 | 0.15 | 0 | 99.56 | 622.87 | -0.36 | 0 | 17.17 | NaN | 40.5
2020-12-29 | 0 | -13.7 | 50.6 | 5958.23 | -0.03 | 0.14 | 0 | 99.62 | 617.83 | -0.27 | 0 | 17.03 | NaN | 38.99
2020-12-29 00:30 | 0 | 0 | 158.36 | 5682.22 | -0.04 | 0.14 | 0 | 99.5 | 588.24 | -0.24 | 0 | 16.99 | NaN | 39.1
2020-12-29 01:00 | 0 | 0 | 218.66 | 5478.84 | -0.03 | 0.14 | 0 | 99.61 | 528.15 | -0.27 | 0 | 16.92 | NaN | 41.61
2020-12-29 01:30 | 0 | 0 | 342.85 | 5168.26 | -0.03 | 0.14 | 0 | 99.24 | 450.12 | -0.27 | 0 | 16.99 | NaN | 41.64
2020-12-29 02:00 | 0 | 0 | 423.06 | 4903.63 | -0.04 | 0.13 | 0 | 99.43 | 446.57 | -0.33 | 0 | 17.12 | NaN | 39.66
2020-12-29 02:30 | 0 | 0 | 487.13 | 4823.48 | -0.03 | 0.13 | 0 | 99.58 | 381.2 | -0.26 | 0 | 17.45 | NaN | 39.22
2020-12-29 03:00 | 0 | 0 | 538.4 | 4719.44 | -0.03 | 0.13 | 0 | 99.68 | 341.94 | -0.27 | 0 | 17.7 | NaN | 39.12
2020-12-29 03:30 | 0 | 0 | 663.43 | 4593.7 | -0.03 | 0.13 | 0 | 99.54 | 320.26 | -0.27 | 0 | 18.03 | NaN | 38.89
2020-12-29 04:00 | 0 | 0 | 615.22 | 4691.3 | -0.03 | 0.13 | 0 | 99.5 | 282.98 | -0.18 | 0.2 | 18.12 | NaN | 38.89
2020-12-29 04:30 | 0 | 0 | 477.64 | 4909.58 | -0.03 | 0.14 | 0 | 99.51 | 360.96 | -0.36 | 4.27 | 18.37 | NaN | 40.84
2020-12-29 05:00 | 0 | 0 | 443.64 | 5034.54 | -0.03 | 0.11 | 0 | 99.67 | 351.58 | 0.23 | 28.72 | 18.56 | NaN | 41.7
2020-12-29 05:30 | 0 | 0 | 446.09 | 5207.78 | -0.03 | 0.13 | 0 | 99.76 | 359.96 | 31.5 | 75.14 | 18.45 | NaN | 41.95
2020-12-29 06:00 | 0 | 0 | 579.89 | 5132.87 | -0.03 | 0.13 | 0 | 99.49 | 358.68 | 190.38 | 139.23 | 17.81 | NaN | 41.23
2020-12-29 06:30 | 0 | 0 | 751.66 | 4916.23 | -0.03 | 0.13 | 0 | 99.46 | 353.17 | 434.84 | 239.98 | 17.44 | NaN | 36.44
2020-12-29 07:00 | 0 | 0 | 672.07 | 4869.19 | -0.03 | 0.13 | 0 | 169.51 | 344.88 | 607.26 | 360.42 | 17.32 | NaN | 35.77
2020-12-29 07:30 | 0 | 0 | 811.7 | 4614.79 | -0.03 | 0.13 | 0 | 436.56 | 364.92 | 709.95 | 499.43 | 17.31 | NaN | 33.62
2020-12-29 08:00 | 0 | 0 | 1066.45 | 4436.16 | -0.03 | 0.12 | 0 | 406.88 | 397.34 | 741.39 | 636.24 | 17.45 | NaN | 36.03
2020-12-29 08:30 | 0 | 0 | 847.9 | 4757.01 | -0.04 | 0.12 | 0 | 275.26 | 411.26 | 769.16 | 817.75 | 18.13 | NaN | 39.04
2020-12-29 09:00 | 0 | 0 | 706.73 | 4838.52 | -0.04 | 0.14 | 0 | 277.33 | 416.39 | 763.8 | 945.39 | 18.88 | NaN | 37.03
2020-12-29 09:30 | 0 | 0 | 676.18 | 4906.09 | -0.03 | 0.13 | 0 | 266.61 | 413.68 | 787.08 | 941.66 | 19.1 | NaN | 38.56
2020-12-29 10:00 | 0 | 0 | 478.68 | 5069.25 | -0.03 | 0.12 | 0 | 265.62 | 448.24 | 826.1 | 959.98 | 19.25 | NaN | 38.46
2020-12-29 10:30 | 0 | 0 | 437.6 | 5207.26 | -0.03 | 0.11 | 0 | 249.62 | 417.91 | 806.66 | 1050.32 | 19.18 | NaN | 39.51
2020-12-29 11:00 | 0 | 0 | 668.41 | 4883.43 | -0.04 | 0.13 | 0 | 246.6 | 369.09 | 835.59 | 1093.18 | 19.58 | NaN | 35.73
2020-12-29 11:30 | 0 | 0 | 887.01 | 4613.16 | -0.03 | 0.14 | 0 | 284.48 | 328.98 | 854.33 | 1033.59 | 19.55 | NaN | 35.51
2020-12-29 12:00 | 0 | 0 | 804.34 | 4809.82 | -0.03 | 0.14 | 0 | 244.42 | 316.72 | 909.95 | 983.69 | 19.66 | NaN | 40.72
2020-12-29 12:30 | 0 | 0 | 801.18 | 4752.07 | -0.03 | 0.13 | 0 | 245.12 | 343.59 | 949.01 | 994.76 | 19.64 | NaN | 38.8
2020-12-29 13:00 | 0 | 0 | 834.46 | 4558.63 | -0.04 | 0.14 | 0 | 239.88 | 342.05 | 1028.07 | 1078.7 | 19.88 | NaN | 36.34
2020-12-29 13:30 | 0 | 0 | 803.87 | 4416.32 | -0.04 | 0.13 | 0 | 237.29 | 379.47 | 1080.01 | 1093.73 | 20.22 | NaN | 35.51
2020-12-29 14:00 | 0 | 0 | 717.37 | 4453.08 | -0.03 | 0.13 | 0 | 252.69 | 388.43 | 1054.35 | 962.83 | 20.16 | NaN | 32.61
2020-12-29 14:30 | 0 | 0 | 566.59 | 4777.09 | -0.03 | 0.12 | 0 | 250.41 | 412.65 | 999.11 | 894.48 | 19.63 | NaN | 38.24
2020-12-29 15:00 | 0 | 0 | 474.24 | 4927.53 | -0.03 | 0.13 | 0 | 243.56 | 426.83 | 988.97 | 832.13 | 19.57 | NaN | 38.22
2020-12-29 15:30 | 0 | 0 | 471.31 | 5068.21 | -0.03 | 0.13 | 0 | 248.92 | 466.34 | 936.98 | 752.25 | 19.52 | NaN | 37.63
2020-12-29 16:00 | 0 | 0 | 381.9 | 5350.64 | -0.03 | 0.11 | 0 | 246.65 | 482.69 | 892.11 | 587.99 | 19.48 | NaN | 35.97
2020-12-29 16:30 | 0 | 0 | 366.66 | 5551.27 | -0.03 | 0.11 | 0 | 208.24 | 488.8 | 895.88 | 442.55 | 19.31 | NaN | 13.41
2020-12-29 17:00 | 0 | 0 | 316.41 | 5717.18 | -0.02 | 0.13 | 0 | 292.64 | 514.93 | 870.24 | 311.03 | 19.04 | NaN | 32.13
2020-12-29 17:30 | 0 | 0 | 364.84 | 5897.69 | -0.03 | 0.11 | 0 | 266.88 | 510.51 | 753.86 | 196.99 | 18.9 | NaN | 31.15
2020-12-29 18:00 | 0 | 0 | 419.67 | 6043.49 | -0.03 | 0.11 | 0 | 133.54 | 569.06 | 589.35 | 109 | 18.69 | NaN | 34.37
2020-12-29 18:30 | 0 | 0 | 369.06 | 6107.44 | -0.02 | 0.11 | 0 | 125.49 | 670.62 | 312.17 | 42.8 | 18.28 | NaN | 37.58
2020-12-29 19:00 | 0 | 0 | 275.77 | 6341.49 | -0.03 | 0.12 | 0 | 101.56 | 735.26 | 88.75 | 8.37 | 18.22 | NaN | 39.12
2020-12-29 19:30 | 0 | 0 | 79.23 | 6586.9 | -0.03 | 0.14 | 0 | 101.84 | 817.76 | 4.95 | 0.59 | 18.41 | NaN | 39.42
2020-12-29 20:00 | 0 | -97.11 | 0.65 | 6631.99 | -0.02 | 0.14 | 0 | 101.64 | 868.54 | -0.36 | 0 | 18.8 | NaN | 39.1
2020-12-29 20:30 | 0 | -277.16 | 0 | 6705.2 | -0.03 | 0.13 | 0 | 101.94 | 882.16 | -0.33 | 0 | 18.77 | NaN | 41.29
2020-12-29 21:00 | 0 | -203.55 | 0 | 6579.55 | -0.03 | 0.14 | 0 | 101.84 | 899.55 | -0.4 | 0 | 19.03 | NaN | 38.74
2020-12-29 21:30 | 0 | -221.05 | 0 | 6501.44 | -0.02 | 0.14 | 0 | 101.99 | 983.72 | -0.36 | 0 | 19.01 | NaN | 39.15
2020-12-29 22:00 | 0 | -162.57 | 0 | 6346.07 | -0.03 | 0.14 | 0 | 101.84 | 1002.27 | -0.37 | 0 | 18.88 | NaN | 37.79
2020-12-29 22:30 | 0 | -175.96 | 0 | 6417.76 | -0.03 | 0.15 | 0 | 101.9 | 979.86 | -0.37 | 0 | 18.54 | NaN | 41.17
2020-12-29 23:00 | 0 | -81.83 | 5.58 | 6115.73 | -0.03 | 0.15 | 0 | 101.91 | 1003.38 | -0.4 | 0 | 18.25 | NaN | 38.69
2020-12-29 23:30 | 0 | -185.5 | 0 | 6101.83 | -0.03 | 0.14 | 0 | 102.04 | 1013.04 | -0.36 | 0 | 18.2 | NaN | 39.08
2020-12-30 | 0 | -177.58 | 0 | 6026.08 | -0.03 | 0.14 | 0 | 101.96 | 985.42 | -0.39 | 0 | 18.2 | NaN | 38.49
2020-12-30 00:30 | 0 | -119.69 | 0 | 5841.13 | -0.03 | 0.14 | 0 | 101.97 | 932.68 | -0.39 | 0 | 18.2 | NaN | 38.94
2020-12-30 01:00 | 0 | -41.37 | 26.27 | 5518.22 | -0.03 | 0.14 | 0 | 101.83 | 917.02 | -0.36 | 0 | 18.21 | NaN | 40.03
2020-12-30 01:30 | 0 | 0 | 228.18 | 5037.19 | -0.03 | 0.14 | 0 | 102.02 | 905.25 | -0.39 | 0 | 18.28 | NaN | 39.22
2020-12-30 02:00 | 0 | 0 | 362.49 | 4657.43 | -0.03 | 0.14 | 0 | 102.06 | 873.42 | -0.39 | 0 | 18.3 | NaN | 37.07
2020-12-30 02:30 | 0 | 0 | 389.41 | 4538.75 | -0.04 | 0.14 | 0 | 101.59 | 881.93 | -0.37 | 0 | 18.29 | NaN | 38.45
2020-12-30 03:00 | 0 | 0 | 403.92 | 4430.42 | -0.04 | 0.15 | 0 | 101.77 | 904.98 | -0.37 | 0 | 18.21 | NaN | 36.48
2020-12-30 03:30 | 0 | 0 | 408.59 | 4398.88 | -0.03 | 0.14 | 0 | 101.84 | 895.24 | -0.36 | 0 | 18.12 | NaN | 36.27
2020-12-30 04:00 | 0 | 0 | 388.84 | 4423.84 | -0.04 | 0.14 | 0 | 101.87 | 900.81 | -0.36 | 0.06 | 18.19 | NaN | 38.07
2020-12-30 04:30 | 0 | 0 | 291.76 | 4652.6 | -0.04 | 0.14 | 0 | 102.06 | 889.43 | -0.37 | 2.78 | 18.3 | NaN | 39.28
2020-12-30 05:00 | 0 | 0 | 222.05 | 4870.93 | -0.03 | 0.15 | 0 | 101.86 | 839.97 | 0.45 | 28.59 | 18.47 | NaN | 40.59
2020-12-30 05:30 | 0 | 0 | 141.8 | 5081.81 | -0.04 | 0.12 | 0 | 101.89 | 830.91 | 47.21 | 97.81 | 18.5 | NaN | 38.74
2020-12-30 06:00 | 0 | 0 | 180.86 | 4946.2 | -0.04 | 0.12 | 0 | 101.98 | 812.59 | 272.66 | 209.06 | 18.52 | NaN | 36
2020-12-30 06:30 | 0 | 0 | 325.2 | 4766.96 | -0.03 | 0.12 | 0 | 102.13 | 739.67 | 564.94 | 352.79 | 18.75 | NaN | 34.37
2020-12-30 07:00 | 0 | 0 | 365.47 | 4719.73 | -0.04 | 0.13 | 0 | 102.15 | 635.69 | 783.82 | 510.74 | 18.81 | NaN | 33.46
2020-12-30 07:30 | 0 | 0 | 482.88 | 4733.36 | -0.04 | 0.28 | 0 | 101.86 | 526.5 | 876.9 | 654.09 | 18.91 | NaN | 32.37
2020-12-30 08:00 | 0 | 0 | 288.51 | 5060.73 | -0.03 | 0.57 | 0 | 101.94 | 469.47 | 929.19 | 777.15 | 19.22 | NaN | 36.19
2020-12-30 08:30 | 0 | 0 | 353.19 | 5142.95 | -0.04 | 0.57 | 0 | 101.75 | 430.59 | 974.05 | 911.26 | 19.88 | NaN | 35.99
2020-12-30 09:00 | 0 | 0 | 403.28 | 5117.82 | -0.04 | 0.45 | 0 | 101.89 | 378.91 | 967.31 | 1038.74 | 20.24 | NaN | 35.51
2020-12-30 09:30 | 0 | 0 | 363.64 | 5102.59 | -0.03 | 0.14 | 0 | 263.16 | 359.81 | 972.99 | 1158.69 | 21.02 | NaN | 37.03
2020-12-30 10:00 | 0 | 0 | 319.82 | 5114.3 | -0.03 | 0.14 | 0 | 252.11 | 323.5 | 1007.03 | 1299.2 | 21.84 | NaN | 39.08
2020-12-30 10:30 | 0 | 0 | 398.73 | 4896.95 | -0.03 | 0.13 | 0 | 258.19 | 283.57 | 1026.59 | 1457.53 | 22.73 | NaN | 34.06
2020-12-30 11:00 | 0 | 0 | 497.04 | 4777.2 | -0.03 | 0.13 | 0 | 258.99 | 270.53 | 1032.78 | 1511.36 | 23.58 | NaN | 32.46
2020-12-30 11:30 | 0 | 0 | 514.19 | 4698.94 | -0.03 | 0.12 | 0 | 256.58 | 253.67 | 1053.77 | 1495.44 | 23.35 | NaN | 32.29
2020-12-30 12:00 | 0 | 0 | 601.04 | 4653.45 | -0.03 | 0.12 | 0 | 254.77 | 244.29 | 1012.7 | 1426.68 | 23.63 | NaN | 34.5
2020-12-30 12:30 | -41.21 | 0 | 551.31 | 4686.68 | -0.03 | 0.12 | 0 | 261.04 | 274.24 | 1016.18 | 1361 | 23.19 | NaN | 34.16
2020-12-30 13:00 | -200.73 | 0 | 610.45 | 4833.08 | -0.02 | 0.13 | 0 | 266.25 | 311.12 | 980.91 | 1319.05 | 23.54 | NaN | 37.9
2020-12-30 13:30 | -200.44 | 0 | 611.86 | 4865.99 | -0.02 | 0.11 | 0 | 252.35 | 382.67 | 981.61 | 1220.68 | 23.24 | NaN | 36.95
2020-12-30 14:00 | -200.39 | 0 | 503.65 | 4996.55 | -0.02 | 0.11 | 0 | 242.69 | 406.88 | 990.25 | 1070.79 | 22.75 | NaN | 37.67
2020-12-30 14:30 | -200.04 | 0 | 413.2 | 5238.28 | -0.02 | 0.11 | 0 | 229.26 | 387.95 | 1023.01 | 963.13 | 22.36 | NaN | 38.4
2020-12-30 15:00 | -200.23 | 0 | 444.69 | 5260.03 | -0.02 | 0.1 | 0 | 276.19 | 407.61 | 953.2 | 893.26 | 22.19 | NaN | 35.98
2020-12-30 15:30 | -200.41 | 0 | 320.6 | 5588.12 | -0.02 | 0.12 | 0 | 309.2 | 476.21 | 856.47 | 760.52 | 21.92 | NaN | 38.34
2020-12-30 16:00 | -200.57 | 0 | 427.11 | 5878.52 | -0.02 | 0.1 | 0 | 101.94 | 535.01 | 738.36 | 622.48 | 21.57 | NaN | 38.97
2020-12-30 16:30 | -200.27 | 0 | 411.78 | 5994.26 | -0.02 | 0.11 | 0 | 107.12 | 604.17 | 755.88 | 486.94 | 21.47 | NaN | 39.68
2020-12-30 17:00 | -52.6 | 0 | 330.54 | 5959.41 | -0.03 | 0.1 | 0 | 132.91 | 736.39 | 650.85 | 365.98 | 21.16 | NaN | 39.17
2020-12-30 17:30 | 0 | 0 | 273.07 | 5953.52 | -0.02 | 0.12 | 0 | 132.73 | 814.81 | 604.04 | 255.21 | 21 | NaN | 33.13
2020-12-30 18:00 | 0 | 0 | 271.27 | 6109.3 | -0.02 | 0.13 | 0 | 132.92 | 791.55 | 480.51 | 143.08 | 20.81 | NaN | 38.93
2020-12-30 18:30 | 0 | 0 | 219.17 | 6388.65 | -0.02 | 0.11 | 0 | 122.63 | 817.58 | 214.61 | 51.73 | 20.53 | NaN | 39.15
2020-12-30 19:00 | 0 | 0 | 144.72 | 6444.08 | -0.02 | 0.12 | 0 | 101.89 | 899.44 | 61.19 | 10.01 | 20.31 | NaN | 38.98
2020-12-30 19:30 | 0 | 0 | 127.73 | 6524.19 | -0.02 | 0.14 | 0 | 101.94 | 926.31 | 2.67 | 0.77 | 20.02 | NaN | 40.42
2020-12-30 20:00 | 0 | 0 | 123.83 | 6486.42 | -0.02 | 0.14 | 0 | 101.79 | 947.19 | -0.37 | 0 | 19.73 | NaN | 45.74
2020-12-30 20:30 | 0 | 0 | 143.9 | 6365.31 | -0.02 | 0.14 | 0 | 101.92 | 922.04 | -0.36 | 0 | 19.51 | NaN | 38.84
2020-12-30 21:00 | 0 | 0 | 174.91 | 6214.26 | -0.02 | 0.13 | 0 | 101.75 | 910.12 | -0.36 | 0 | 19.22 | NaN | 37.85
2020-12-30 21:30 | 0 | 0 | 158.16 | 6256.65 | -0.02 | 0.14 | 0 | 101.75 | 895.03 | -0.37 | 0 | 18.92 | NaN | 38.72
2020-12-30 22:00 | 0 | 0 | 335.57 | 5979.06 | -0.02 | 0.14 | 0 | 101.64 | 872.51 | -0.37 | 0 | 18.67 | NaN | 35.95
2020-12-30 22:30 | 0 | 0 | 295.39 | 6074.32 | -0.02 | 0.14 | 0 | 101.95 | 853.66 | -0.37 | 0 | 18.8 | NaN | 40.35
2020-12-30 23:00 | 0 | 0 | 392.99 | 5797.96 | -0.02 | 0.14 | 0 | 101.75 | 843.93 | -0.37 | 0 | 19.15 | NaN | 35.58
2020-12-30 23:30 | 0 | 0 | 230.44 | 5908.33 | -0.03 | 0.14 | 0 | 102.02 | 817.12 | -0.33 | 0 | 19.37 | NaN | 39.88
2020-12-31 | 0 | 0 | 250.78 | 5807.22 | -0.03 | 0.14 | 0 | 101.84 | 770.04 | -0.36 | 0 | 19.42 | NaN | 38.84
2020-12-31 00:30 | 0 | 0 | 330.08 | 5575.73 | -0.03 | 0.14 | 0 | 101.77 | 757.75 | -0.36 | 0 | 19.56 | NaN | 35.93
2020-12-31 01:00 | 0 | 0 | 520.01 | 5167.36 | -0.03 | 0.14 | 0 | 101.62 | 755.45 | -0.36 | 0 | 19.47 | NaN | 35.6
2020-12-31 01:30 | 0 | 0 | 675.48 | 4646.23 | -0.03 | 0.14 | 0 | 101.82 | 782.39 | -0.36 | 0 | 19.08 | NaN | 34.19
2020-12-31 02:00 | 0 | 0 | 798.98 | 4331.92 | -0.03 | 0.13 | 0 | 101.73 | 789.02 | -0.36 | 0 | 18.97 | NaN | 34.92
2020-12-31 02:30 | 0 | 0 | 774.01 | 4229.52 | -0.03 | 0.14 | 0 | 101.48 | 763.48 | -0.4 | 0 | 18.65 | NaN | 35.13
2020-12-31 03:00 | 0 | 0 | 781.13 | 4139.34 | -0.03 | 0.14 | 0 | 101.81 | 814.08 | -0.36 | 0 | 18.46 | NaN | 31.41
2020-12-31 03:30 | 0 | 0 | 792.06 | 4059.2 | -0.04 | 0.14 | 0 | 101.85 | 823.14 | -0.36 | 0 | 18.68 | NaN | 30.93
2020-12-31 04:00 | 0 | 0 | 828.36 | 4076.97 | -0.04 | 0.13 | 0 | 101.57 | 805.11 | -0.36 | 0.09 | 19.06 | NaN | 32.61
2020-12-31 04:30 | 0 | 0 | 762.02 | 4239.58 | -0.04 | 0.13 | 0 | 101.57 | 795.63 | -0.27 | 3.66 | 19.38 | NaN | 36.26
2020-12-31 05:00 | 0 | 0 | 702.22 | 4390.16 | -0.04 | 0.12 | 0 | 101.61 | 782.7 | 0.27 | 36.29 | 19.77 | NaN | 33.37
2020-12-31 05:30 | 0 | 0 | 706.35 | 4533.32 | -0.03 | 0.11 | 0 | 101.42 | 772.74 | 32.94 | 117.97 | 20.18 | NaN | 37.08
2020-12-31 06:00 | 0 | 0 | 696.83 | 4515.75 | -0.03 | 0.11 | 0 | 117.64 | 741.57 | 143.86 | 235.79 | 20.64 | NaN | 34.18
2020-12-31 06:30 | 0 | 0 | 788.49 | 4480.43 | -0.03 | 0.12 | 0 | 151.43 | 722.98 | 278.59 | 407.56 | 20.99 | NaN | 21.12
2020-12-31 07:00 | 0 | 0 | 681.57 | 4378.81 | -0.03 | 0.12 | 0 | 196.45 | 697.22 | 498.81 | 591.41 | 21.47 | NaN | 29.04
2020-12-31 07:30 | 0 | 0 | 411.57 | 4566.01 | -0.03 | 0.2 | 0 | 307.18 | 692.45 | 658.24 | 743.38 | 22.02 | NaN | 34.17
2020-12-31 08:00 | 0 | 0 | 351.99 | 4681.96 | -0.03 | 0.21 | 0 | 312.47 | 638.5 | 829.79 | 895.84 | 22.32 | NaN | 41.57
2020-12-31 08:30 | 0 | 0 | 339.31 | 4758.5 | -0.03 | 0.2 | 0 | 264.39 | 567.37 | 975.9 | 1059.8 | 22.92 | NaN | 38.72
2020-12-31 09:00 | 0 | 0 | 381.81 | 4702.32 | -0.03 | 0.19 | 0 | 281.78 | 487.83 | 969.96 | 1198.99 | 23.33 | NaN | 34.98
2020-12-31 09:30 | 0 | 0 | 316.87 | 4881.53 | -0.03 | 0.17 | 0 | 262.74 | 438.9 | 1035.1 | 1305.21 | 23.47 | NaN | 43.91
2020-12-31 10:00 | 0 | 0 | 236.39 | 4979.05 | -0.03 | 0.16 | 0 | 248.73 | 405.59 | 1044.32 | 1369.13 | 24.01 | NaN | 38.17
2020-12-31 10:30 | 0 | 0 | 304.93 | 4951.07 | -0.03 | 0.14 | 0 | 246.64 | 405.75 | 1082.06 | 1383.07 | 23.62 | NaN | 38.14
2020-12-31 11:00 | 0 | 0 | 317.93 | 4941.63 | -0.03 | 0.14 | 0 | 235.26 | 412.07 | 1066.94 | 1354.71 | 23.44 | NaN | 37.44
2020-12-31 11:30 | 0 | 0 | 228.04 | 5033.35 | -0.02 | 0.13 | 0 | 232.5 | 434.23 | 1075.98 | 1324.09 | 22.87 | NaN | 36.63
2020-12-31 12:00 | 0 | 0 | 307.05 | 5108.45 | -0.02 | 0.14 | 0 | 240.91 | 380.89 | 988.76 | 1250.62 | 22.28 | NaN | 38.36
2020-12-31 12:30 | 0 | 0 | 392.66 | 5150.5 | -0.03 | 0.13 | 0 | 224.49 | 345.51 | 890.05 | 1197.76 | 22.02 | NaN | 36.92
2020-12-31 13:00 | 0 | 0 | 440.94 | 5054.01 | -0.03 | 0.15 | 0 | 223.97 | 379.64 | 888.45 | 1123.4 | 21.8 | NaN | 33.44
2020-12-31 13:30 | 0 | 0 | 530.45 | 5037.32 | -0.03 | 0.13 | 0 | 239.08 | 421.42 | 838.38 | 1086.79 | 21.43 | NaN | 21.97
2020-12-31 14:00 | 0 | 0 | 567.89 | 4995.13 | -0.02 | 0.12 | 0 | 258.82 | 471.97 | 703.61 | 1088.15 | 20.93 | NaN | 27.51
2020-12-31 14:30 | 0 | 0 | 571.17 | 5083.35 | -0.02 | 0.14 | 0 | 258.33 | 505.44 | 578.63 | 980.04 | 20.38 | NaN | 31.51
2020-12-31 15:00 | 0 | 0 | 505.95 | 5164.98 | -0.02 | 0.13 | 0 | 267.4 | 598.36 | 623.84 | 812.35 | 20.03 | NaN | 36.48
2020-12-31 15:30 | 0 | 0 | 330.1 | 5341.29 | -0.02 | 0.13 | 0 | 314.93 | 697.61 | 524.56 | 685.42 | 19.83 | NaN | 35.73
2020-12-31 16:00 | 0 | 0 | 205.24 | 5673.51 | -0.02 | 0.12 | 0 | 273.61 | 721.49 | 532.18 | 562.21 | 19.8 | NaN | 38.52
2020-12-31 16:30 | 0 | 0 | 366.85 | 5825.97 | -0.02 | 0.12 | 0 | 292.7 | 702.51 | 410.81 | 420.02 | 19.82 | NaN | 22.28
2020-12-31 17:00 | 0 | 0 | 486.88 | 5842.59 | -0.02 | 0.12 | 0 | 297.58 | 735.29 | 319.05 | 295.34 | 19.98 | NaN | 36.21
2020-12-31 17:30 | 0 | 0 | 422.67 | 5763.79 | -0.01 | 0.13 | 0 | 294.56 | 824.41 | 267.09 | 182.85 | 20.17 | NaN | 35.97
2020-12-31 18:00 | 0 | 0 | 385.99 | 5757.68 | -0.01 | 0.12 | 0 | 308.85 | 951.55 | 147.28 | 90.77 | 20.18 | NaN | 35.97
2020-12-31 18:30 | 0 | 0 | 345.55 | 5705.1 | -0.02 | 0.13 | 0 | 325.8 | 984.68 | 78.91 | 32.57 | 20.03 | NaN | 31.81
2020-12-31 19:00 | 0 | 0 | 200.39 | 5816.25 | -0.02 | 0.12 | 0 | 350.36 | 1022.56 | 18.57 | 6.27 | 19.99 | NaN | 39.25
2020-12-31 19:30 | 0 | 0 | 183.05 | 5656.79 | -0.02 | 0.14 | 0 | 486.73 | 1015.39 | 0.62 | 0.45 | 19.91 | NaN | 43.08
2020-12-31 20:00 | 0 | 0 | 276.48 | 5468.43 | -0.02 | 0.14 | 0 | 548.78 | 1000.11 | -0.37 | 0 | 19.78 | NaN | 42.6
2020-12-31 20:30 | 0 | 0 | 494.52 | 5258.69 | -0.02 | 0.15 | 0 | 423.48 | 982.93 | -0.36 | 0 | 19.44 | NaN | 40.34
2020-12-31 21:00 | 0 | 0 | 490.16 | 5265.14 | -0.02 | 0.15 | 0 | 431.14 | 962.2 | -0.36 | 0 | 19.13 | NaN | 38.05
2020-12-31 21:30 | 0 | 0 | 574.9 | 5192.02 | -0.02 | 0.13 | 0 | 445.28 | 970.3 | -0.33 | 0 | 18.82 | NaN | 39.01
2020-12-31 22:00 | 0 | 0 | 625.73 | 5238.89 | -0.02 | 0.13 | 0 | 455.17 | 911.43 | -0.37 | 0 | 18.59 | NaN | 39.57
2020-12-31 22:30 | 0 | 0 | 504.37 | 5525.87 | -0.02 | 0.13 | 0 | 362.21 | 856.3 | -0.4 | 0 | 18.88 | NaN | 53.86
2020-12-31 23:00 | 0 | 0 | 531.73 | 5542.38 | -0.03 | 0.15 | 0 | 288.53 | 828.2 | -0.34 | 0 | 18.64 | NaN | 41.42
2020-12-31 23:30 | 0 | 0 | 413.35 | 5647.2 | -0.02 | 0.14 | 0 | 302.04 | 804.61 | -0.3 | 0 | 18.34 | NaN | 50.7
2021-01-01 | 0 | 0 | 580.32 | 5383.81 | -0.02 | 0.14 | 0 | 248.65 | 812.41 | -0.36 | 0 | 18.22 | NaN | 43.29
2021-01-01 00:30 | 0 | 0 | 392.98 | 5198.03 | -0.03 | 0.14 | 0 | 372.8 | 854.28 | -0.37 | 0 | 18.2 | NaN | 38.04
2021-01-01 01:00 | 0 | 0 | 224 | 5252.9 | -0.03 | 0.14 | 0 | 196.21 | 910 | -0.36 | 0 | 18.19 | NaN | 38.1
2021-01-01 01:30 | 0 | 0 | 440.61 | 4776.56 | -0.03 | 0.14 | 0 | 161.55 | 901.18 | -0.36 | 0 | 18.12 | NaN | 32.26
2021-01-01 02:00 | 0 | 0 | 554.82 | 4467.91 | -0.03 | 0.13 | 0 | 163.33 | 845.17 | -0.36 | 0 | 18.08 | NaN | 32.45
2021-01-01 02:30 | 0 | 0 | 559.15 | 4275.63 | -0.03 | 0.15 | 0 | 158.34 | 851.22 | -0.33 | 0 | 17.93 | NaN | 27.76
2021-01-01 03:00 | 0 | 0 | 574.52 | 4175.61 | -0.03 | 0.15 | 0 | 153.21 | 879.57 | -0.39 | 0 | 17.92 | NaN | 26.83
2021-01-01 03:30 | 0 | 0 | 530.42 | 4121.1 | -0.03 | 0.14 | 0 | 148.63 | 874.47 | -0.36 | 0 | 18.08 | NaN | 25.64
2021-01-01 04:00 | 0 | 0 | 566.94 | 4119.77 | -0.03 | 0.14 | 0 | 134.94 | 867.76 | -0.36 | 0.05 | 18.28 | NaN | 26.31
2021-01-01 04:30 | 0 | 0 | 636.12 | 4141.59 | -0.03 | 0.14 | 0 | 103.44 | 844.39 | -0.37 | 2.07 | 18.48 | NaN | 29.42
2021-01-01 05:00 | 0 | 0 | 672.94 | 4158.86 | -0.03 | 0.14 | 0 | 103.36 | 798.17 | -0.32 | 22.24 | 18.69 | NaN | 31.15
2021-01-01 05:30 | 0 | 0 | 653.16 | 4125.89 | -0.03 | 0.12 | 0 | 122.25 | 856.57 | 13.08 | 83.54 | 18.97 | NaN | 29.75
2021-01-01 06:00 | 0 | 0 | 598.46 | 4069.27 | -0.03 | 0.12 | 0 | 156.74 | 867.56 | 95.07 | 174.62 | 19.22 | NaN | 25.53
2021-01-01 06:30 | 0 | 0 | 559.49 | 4061.64 | -0.03 | 0.12 | 0 | 146.87 | 863.6 | 180.94 | 314.57 | 19.76 | NaN | 19.57
2021-01-01 07:00 | 0 | 0 | 600.48 | 4055.7 | -0.03 | 0.12 | 0 | 131.19 | 852.21 | 229.05 | 458.77 | 20.38 | NaN | 6.91
2021-01-01 07:30 | 0 | 0 | 607.54 | 4062.59 | -0.03 | 0.12 | 0 | 223.45 | 814.82 | 257.44 | 564.98 | 20.49 | NaN | 20.82
2021-01-01 08:00 | 0 | 0 | 685.98 | 4062.82 | -0.03 | 0.1 | 0 | 197.13 | 772.43 | 392.39 | 683.54 | 20.44 | NaN | 12.79
2021-01-01 08:30 | 0 | 0 | 729.3 | 4087.7 | -0.03 | 0.1 | 0 | 197.16 | 787.29 | 422.52 | 795.04 | 20.67 | NaN | 20.69
2021-01-01 09:00 | 0 | 0 | 780.82 | 4098.05 | -0.03 | 0.11 | 0 | 186.1 | 786.22 | 450.5 | 889.89 | 20.96 | NaN | 26.99
2021-01-01 09:30 | 0 | 0 | 774.81 | 4120.14 | -0.03 | 0.11 | 0 | 205.68 | 739.16 | 530.02 | 1012.04 | 21.09 | NaN | 31.89
2021-01-01 10:00 | 0 | 0 | 799.63 | 4064.02 | -0.03 | 0.11 | 0 | 250.77 | 655.19 | 577.66 | 1081.69 | 21.17 | NaN | 30.53
2021-01-01 10:30 | 0 | 0 | 888.43 | 4089.37 | -0.03 | 0.1 | 0 | 255.64 | 561.29 | 637.33 | 1094.95 | 21.07 | NaN | 27.17
2021-01-01 11:00 | 0 | 0 | 925.45 | 4085.09 | -0.02 | 0.11 | 0 | 254.51 | 496.85 | 710.11 | 1114.49 | 21.34 | NaN | 27.81
2021-01-01 11:30 | 0 | 0 | 1033.47 | 4114.71 | -0.03 | 0.11 | 0 | 263.26 | 401.9 | 719.74 | 1069.62 | 21.49 | NaN | 27.66
2021-01-01 12:00 | 0 | 0 | 1111.51 | 4130.46 | -0.03 | 0.11 | 0 | 285.43 | 395.99 | 642.96 | 1016.59 | 21.55 | NaN | 31.01
2021-01-01 12:30 | 0 | 0 | 1091.72 | 4151.11 | -0.03 | 0.1 | 0 | 327.95 | 391.35 | 582.8 | 956.48 | 21.24 | NaN | 33.34
2021-01-01 13:00 | 0 | 0 | 1038.55 | 4189.77 | -0.02 | 0.11 | 0 | 267.42 | 409.5 | 658.51 | 903.73 | 20.93 | NaN | 32.54
2021-01-01 13:30 | 0 | 0 | 971.09 | 4153.82 | -0.02 | 0.12 | 0 | 294.17 | 437.36 | 653.08 | 873.84 | 20.64 | NaN | 30.23
2021-01-01 14:00 | 0 | 0 | 798.81 | 4159.45 | -0.02 | 0.11 | 0 | 336.3 | 467.82 | 740.87 | 797.2 | 20.52 | NaN | 32.5
2021-01-01 14:30 | 0 | 0 | 714.8 | 4213.62 | -0.02 | 0.12 | 0 | 284 | 505.32 | 836.94 | 739.6 | 20.51 | NaN | 31.1
2021-01-01 15:00 | 0 | 0 | 998.88 | 4205.16 | -0.02 | 0.12 | 0 | 109.1 | 561.21 | 711.57 | 682.15 | 20.58 | NaN | 32.5
2021-01-01 15:30 | 0 | 0 | 1065.91 | 4242.43 | -0.02 | 0.13 | 0 | 134.64 | 567.03 | 646.17 | 578.96 | 20.57 | NaN | 32.79
2021-01-01 16:00 | 0 | 0 | 1192.41 | 4441.86 | -0.02 | 0.11 | 0 | 134.63 | 578.36 | 512.27 | 475.45 | 20.29 | NaN | 37.3
2021-01-01 16:30 | 0 | 0 | 1164.8 | 4679.86 | -0.02 | 0.1 | 0 | 134.37 | 595.12 | 450.65 | 369.24 | 19.71 | NaN | 36.04
2021-01-01 17:00 | 0 | 0 | 927.21 | 5074.8 | -0.02 | 0.09 | 0 | 134.49 | 637.55 | 360.89 | 267.82 | 19.42 | NaN | 39.73
2021-01-01 17:30 | 0 | 0 | 718.51 | 5381.09 | -0.01 | 0.12 | 0 | 134.57 | 705.93 | 279.14 | 179 | 18.47 | NaN | 34.97
2021-01-01 18:00 | 0 | 0 | 564.34 | 5594.02 | -0.01 | 0.12 | 0 | 134.74 | 769.45 | 179.86 | 104.93 | 17.93 | NaN | 36.67
2021-01-01 18:30 | 0 | 0 | 415.86 | 5689.72 | -0.01 | 0.1 | 0 | 135.06 | 872.18 | 90.61 | 38.65 | 17.53 | NaN | 38.33
2021-01-01 19:00 | 0 | 0 | 372.87 | 5810.79 | -0.01 | 0.13 | 0 | 134.41 | 849.91 | 18.91 | 6.67 | 17.18 | NaN | 38.46
2021-01-01 19:30 | 0 | 0 | 454.73 | 5943.73 | -0.01 | 0.13 | 0 | 134.5 | 733.38 | -0.1 | 0.4 | 17.19 | NaN | 38.79
2021-01-01 20:00 | 0 | 0 | 443.79 | 5870.36 | -0.01 | 0.14 | 0 | 133.72 | 740.51 | -0.34 | 0 | 17.28 | NaN | 39.04
2021-01-01 20:30 | 0 | 0 | 544.63 | 5663.89 | -0.02 | 0.14 | 0 | 135.39 | 765.06 | -0.33 | 0 | 17.29 | NaN | 38.32
2021-01-01 21:00 | 0 | 0 | 548.47 | 5479.4 | -0.02 | 0.12 | 0 | 135.43 | 845.39 | -0.36 | 0 | 17.22 | NaN | 36.13
2021-01-01 21:30 | 0 | 0 | 569.06 | 5508.12 | -0.02 | 0.14 | 0 | 135.31 | 840.03 | -0.36 | 0 | 17.19 | NaN | 37.29
2021-01-01 22:00 | 0 | 0 | 590.49 | 5390.27 | -0.03 | 0.15 | 0 | 134.55 | 912.34 | -0.37 | 0 | 17.1 | NaN | 35.9
2021-01-01 22:30 | 0 | 0 | 553.37 | 5333.39 | -0.03 | 0.14 | 0 | 134.98 | 981.56 | -0.3 | 0 | 16.92 | NaN | 37.02
2021-01-01 23:00 | 0 | 0 | 588.06 | 5244.55 | -0.03 | 0.14 | 0 | 124.46 | 981.94 | -0.36 | 0 | 16.73 | NaN | 35.92
2021-01-01 23:30 | 0 | 0 | 635.02 | 5100.64 | -0.03 | 0.14 | 0 | 103.42 | 982.3 | -0.36 | 0 | 16.66 | NaN | 36.81
2021-01-02 | 0 | 0 | 701.38 | 4893.54 | -0.03 | 0.14 | 0 | 103.7 | 977.48 | -0.36 | 0 | 16.28 | NaN | 37.12
2021-01-02 00:30 | 0 | 0 | 604.19 | 4818.9 | -0.03 | 0.14 | 0 | 103.66 | 950.77 | -0.36 | 0 | 16.21 | NaN | 36.04
2021-01-02 01:00 | 0 | 0 | 494.04 | 4750.58 | -0.04 | 0.13 | 0 | 103.56 | 905.66 | -0.36 | 0 | 16.29 | NaN | 35.29
2021-01-02 01:30 | 0 | 0 | 469.31 | 4546.17 | -0.04 | 0.14 | 0 | 103.45 | 878.39 | -0.36 | 0 | 16.4 | NaN | 29.7
2021-01-02 02:00 | 0 | 0 | 425.69 | 4420.28 | -0.03 | 0.14 | 0 | 103.86 | 877.22 | -0.37 | 0 | 16.57 | NaN | 24.62
2021-01-02 02:30 | 0 | 0 | 411.63 | 4322.51 | -0.03 | 0.14 | 0 | 103.75 | 876.75 | -0.37 | 0 | 16.6 | NaN | 26.28
2021-01-02 03:00 | 0 | 0 | 332.12 | 4299.02 | -0.03 | 0.14 | 0 | 103.61 | 870.74 | -0.37 | 0 | 16.6 | NaN | 25.4
2021-01-02 03:30 | 0 | 0 | 216.89 | 4377.75 | -0.03 | 0.14 | 0 | 104.01 | 893.37 | -0.37 | 0 | 16.6 | NaN | 24.92
2021-01-02 04:00 | 0 | 0 | 299.35 | 4382.62 | -0.03 | 0.14 | 0 | 103.59 | 844.09 | -0.37 | 0.02 | 16.6 | NaN | 28.55
2021-01-02 04:30 | 0 | 0 | 409.63 | 4344.43 | -0.03 | 0.14 | 0 | 103.69 | 804.7 | -0.37 | 1.82 | 16.62 | NaN | 30.77
2021-01-02 05:00 | 0 | 0 | 495.44 | 4366.72 | -0.03 | 0.12 | 0 | 103.74 | 758.75 | 0.34 | 22.14 | 16.87 | NaN | 31.14
2021-01-02 05:30 | 0 | 0 | 457.03 | 4477.29 | -0.04 | 0.1 | 0 | 103.71 | 726.89 | 27.04 | 82.27 | 17.07 | NaN | 35.61
2021-01-02 06:00 | 0 | 0 | 309.65 | 4663.37 | -0.04 | 0.11 | 0 | 103.49 | 708.49 | 102.81 | 163.43 | 17.13 | NaN | 27.3
2021-01-02 06:30 | 0 | 0 | 521.24 | 4558.61 | -0.03 | 0.13 | 0 | 104.01 | 621.38 | 256.06 | 262.04 | 17.38 | NaN | 26.74
2021-01-02 07:00 | 0 | 0 | 592.03 | 4568.27 | -0.03 | 0.12 | 0 | 103.65 | 588.09 | 345.97 | 398.03 | 17.78 | NaN | 28.03
2021-01-02 07:30 | 0 | 0 | 721.27 | 4613 | -0.03 | 0.07 | 0 | 103.66 | 531.81 | 402.2 | 554.11 | 18.27 | NaN | 31.14
2021-01-02 08:00 | 0 | 0 | 814.46 | 4653.05 | -0.03 | 0.1 | 0 | 103.54 | 500.04 | 467.75 | 669.83 | 18.17 | NaN | 32.67
2021-01-02 08:30 | 0 | 0 | 862.74 | 4725.88 | -0.03 | 0.1 | 0 | 103.74 | 389.9 | 560.83 | 791.67 | 18.28 | NaN | 33.75
2021-01-02 09:00 | 0 | 0 | 833.72 | 4757.95 | -0.03 | 0.12 | 0 | 163.82 | 290.85 | 573.15 | 910.97 | 18.44 | NaN | 35.03
2021-01-02 09:30 | 0 | 0 | 744.36 | 4762.13 | -0.03 | 0.1 | 0 | 281.3 | 232.89 | 596.83 | 986.14 | 18.99 | NaN | 34.53
2021-01-02 10:00 | 0 | 0 | 844.46 | 4732.81 | -0.03 | 0.13 | 0 | 266.56 | 194.75 | 558.21 | 1078.15 | 19.27 | NaN | 32.23
2021-01-02 10:30 | 0 | 0 | 820.32 | 4703.4 | -0.03 | 0.11 | 0 | 246.93 | 179.1 | 619.75 | 1197.5 | 20.22 | NaN | 32.46
2021-01-02 11:00 | 0 | 0 | 735.26 | 4693.24 | -0.03 | 0.13 | 0 | 241.54 | 197.64 | 622.51 | 1207.95 | 21.34 | NaN | 25.21
2021-01-02 11:30 | 0 | 0 | 724.12 | 4677.15 | -0.03 | 0.11 | 0 | 239.32 | 226.6 | 644.06 | 1197.49 | 21.93 | NaN | 23.87
2021-01-02 12:00 | 0 | 0 | 743.55 | 4687.27 | -0.03 | 0.12 | 0 | 237.51 | 264.52 | 584.82 | 1197.34 | 22 | NaN | 25.85
2021-01-02 12:30 | 0 | 0 | 629.92 | 4753.89 | -0.03 | 0.12 | 0 | 235.2 | 280.79 | 576.33 | 1154.34 | 21.22 | NaN | 20.94
2021-01-02 13:00 | 0 | 0 | 632.34 | 4760.38 | -0.02 | 0.11 | 0 | 227.59 | 311.42 | 578.37 | 1071.65 | 20.64 | NaN | 13.56
2021-01-02 13:30 | 0 | 0 | 498.65 | 4730.26 | -0.02 | 0.12 | 0 | 272.48 | 452.65 | 629.61 | 976.97 | 20.16 | NaN | 20.98
2021-01-02 14:00 | 0 | 0 | 492.75 | 4722.82 | -0.03 | 0.12 | 0 | 272.06 | 535.36 | 711.92 | 917.27 | 19.95 | NaN | 24.17
2021-01-02 14:30 | 0 | 0 | 436.12 | 4837.07 | -0.03 | 0.1 | 0 | 315.88 | 544.84 | 669.95 | 814.62 | 20.82 | NaN | 29.59
2021-01-02 15:00 | 0 | 0 | 400.74 | 4904.07 | -0.03 | 0.12 | 0 | 335.42 | 651.97 | 593.27 | 698.57 | 21.18 | NaN | 33.85
2021-01-02 15:30 | 0 | 0 | 421.7 | 4965.72 | -0.03 | 0.12 | 0 | 385.99 | 654.72 | 510.55 | 569.65 | 20.58 | NaN | 32.31
2021-01-02 16:00 | 0 | 0 | 473.36 | 5219.66 | -0.03 | 0.12 | 0 | 385.49 | 610.24 | 486.82 | 451.46 | 19.98 | NaN | 33.24
2021-01-02 16:30 | 0 | 0 | 450.5 | 5330.45 | -0.03 | 0.12 | 0 | 398 | 669.78 | 429.71 | 369.03 | NaN | NaN | 32.02
2021-01-02 17:00 | 0 | 0 | 382.36 | 5558.38 | -0.03 | 0.12 | 0 | 495.23 | 661.16 | 324.64 | 272.17 | NaN | NaN | 37.29
2021-01-02 17:30 | 0 | 0 | 426.22 | 5551.13 | -0.03 | 0.12 | 0 | 470.22 | 704.39 | 255.1 | 212.01 | NaN | NaN | 37.29

## nsw_capacity_data
Region | Technology | Existing+Committed in 2021 (MW)
NSW | Black Coal | 10210
NSW | Brown Coal | 0
NSW | CCGT | 440
NSW | Peaking Gas+Liquids | 1561.233
NSW | Hydro | 2285
NSW | Large-scale Battery | 0
NSW | VPP Battery | 33.3575
NSW | Pumped Hydro | 240
NSW | Wind | 1501.45
NSW | Solar | 1744.286
Total excluding storage |  | 17741.969
NSW | DSP | 93.24
NSW | Distributed PV | 2774.0673
NSW | Other Behind the Meter Battery | 133.43
Total including Distributed PV |  | 20516.0363
Source: AEMO ISP 2020 Central Scenario Generation Outlook (Capacity)

## ramp_rates
Source: GHD AEMO revised - 2018-19 Costs_and_Technical_Parameter
Technical parameters and operating costs
General Unit Details | [6 empty] | Technical Details | [8 empty] | Storage Details |  | Cost Detail
Station name | Unit name | Region | Zone | Generation Type | Fuel Type | Commissioning Date | Installed capacity (MW) | Min Stable Generation (% of installed capacity) | Auxiliary load (% of installed capacity) | Ramp Up Rate (MW/h) - standard operation | Ramp Down Rate (MW/h) - standard operation | Heat rate at maximum operation (GJ/MWh) | Thermal Efficiency (%, HHV sent-out) | Maintenance Frequency (no of maintenance events per year) | Average Planned Maintenance (no of days/year) | Hydro units: Pumping Efficiency (MWh pumped per MWh generated) - within 24 hours | Pump load (MW) | Fixed Operating Cost ($/kW/year) | Variable Op Cost ($/MWh sent-out) | Cold Start-up Notification Time (Hr) | Warm Start-up Notification Time (Hr) | Hot Start-up Notification Time (Hr) | Cold Start-up Costs ($/MW) | Warm Start-up Costs ($/MW) | Hot Start-up Costs ($/MW) | Ramp (%cap/min)
Broken Hill Solar Plant | Broken Hill Solar Plant | NSW |  | Solar | Solar | 2015 | 53 | 0 | 1 | [8 empty] | 25.7 | 0 | [6 empty] | 0%
Condamine | CPSA | QLD | SWQ | CCGT | Natural gas | 2009 | 144 | 0 | 3 | 180 | 180 | 7.2874 | 49.4 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 2.083%
Darling Downs | DDPS1_GT1 | QLD | SWQ | CCGT | Natural gas | 2010 | 121.5 | 0 | 6 | 380 | 380 | 7.377 | 48.8 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 5.213%
Darling Downs | DDPS1_GT2 | QLD | SWQ | CCGT | Natural gas | 2010 | 121.5 | 0 | 6 | 380 | 380 | 7.377 | 48.8 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 5.213%
Darling Downs | DDPS1_GT3 | QLD | SWQ | CCGT | Natural gas | 2010 | 121.5 | 0 | 6 | 380 | 380 | 7.377 | 48.8 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 5.213%
Darling Downs | DDPS1_ST | QLD | SWQ | CCGT | Natural gas | 2010 | 280 | 0 | 6 | 380 | 380 | 7.377 | 48.8 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 2.262%
Swanbank E | SWAN_E | QLD | SEQ | CCGT | Natural gas | 2002 | 385 | 0 | 3 | 640 | 640 | 7.438 | 48.4 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 2.771%
Townsville | YABULU | QLD | NQ | CCGT | Natural gas | 2005 | 160 | 0 | 3 | 340 | 340 | 7.5949 | 47.4 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 3.542%
Townsville | YABULU2 | QLD | NQ | CCGT | Natural gas | 2005 | 84 | 0 | 3 | 340 | 340 | 7.5949 | 47.4 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 6.746%
Osborne | OsborneGT | SA | ADE | CCGT | Natural gas | 1998 | 118 | 0 | 5 | 160 | 160 | 8.1633 | 44.1 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 2.26%
Osborne | OsborneST | SA | ADE | CCGT | Natural gas | 1998 | 62 | 0 | 5 | 160 | 160 | 8.1633 | 44.1 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 4.301%
Pelican Point | PPCCGTGT1 | SA | ADE | CCGT | Natural gas | 2000 | 160 | 0 | 2 | 600 | 600 | 7.3469 | 49 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 6.25%
Pelican Point | PPCCGTGT2 | SA | ADE | CCGT | Natural gas | 2000 | 160 | 0 | 2 | 600 | 600 | 7.3469 | 49 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 6.25%
Pelican Point | PPCCGTST | SA | ADE | CCGT | Natural gas | 2000 | 154 | 0 | 2 | 600 | 600 | 7.3469 | 49 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 6.494%
Tamar Valley CCGT | TVCC201 | TAS | TAS | CCGT | Natural gas | 2010 | 208 | 0 | 3 | 110 | 540 | 7.2874 | 49.4 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 4.327%
Gullen Range Solar Farm | GULLRSF1 | NSW |  | Solar | Solar | 2018 | 10 | 0 | 1 | [8 empty] | 25.7 | 0 | [6 empty] | 0%
Moree Solar Farm | Moree Solar | NSW |  | Solar | Solar | 2016 | 56 | 0 | 1 | [8 empty] | 25.7 | 0 | [6 empty] | 0%
Nyngan Solar Plant | Nyngan | NSW |  | Solar | Solar | 2015 | 102 | 0 | 1 | [8 empty] | 25.7 | 0 | [6 empty] | 0%
White Rock Wind Farm | WHITEROCKWF | NSW |  | Wind | Wind | 2019 | 172.5 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Yarwun CoGen | YARWUN_1 | QLD | CQ | CoGen | Natural gas | 2010 | 180 | 0 | 2 | 600 | 600 | 10.3746 | 34.7 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 5.556%
Capital Wind Farm | CAPTL_WF | NSW |  | Wind | Wind | 2010 | 140.7 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Cullerin Range Wind Farm | CULLRGWF | NSW |  | Wind | Wind | 2009 | 30 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Eraring | ER01 | NSW | NCEN | Steam turbine | Black Coal | 1983 | 720 | 32 | 6 | 300 | 300 | 9.5491 | 37.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.6944%
Eraring | ER02 | NSW | NCEN | Steam turbine | Black Coal | 1983 | 720 | 32 | 6 | 300 | 300 | 9.5491 | 37.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.6944%
Eraring | ER03 | NSW | NCEN | Steam turbine | Black Coal | 1983 | 720 | 32 | 6 | 300 | 300 | 9.5491 | 37.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.6944%
Eraring | ER04 | NSW | NCEN | Steam turbine | Black Coal | 1983 | 720 | 32 | 6 | 300 | 300 | 9.5491 | 37.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.6944%
Vales Point B | VP5 | NSW | NCEN | Steam turbine | Black Coal | 1978 | 660 | 38 | 5 | 290 | 220 | 9.6774 | 37.2 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.7323%
Vales Point B | VP6 | NSW | NCEN | Steam turbine | Black Coal | 1978 | 660 | 38 | 5 | 290 | 220 | 9.6774 | 37.2 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.7323%
Mt Piper | MP1 | NSW | NCEN | Steam turbine | Black Coal | 1993 | 700 | 42 | 5 | 310 | 310 | 9.2545 | 38.9 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.7381%
Mt Piper | MP2 | NSW | NCEN | Steam turbine | Black Coal | 1993 | 700 | 42 | 5 | 310 | 310 | 9.2545 | 38.9 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.7381%
Bayswater | BW01 | NSW | NCEN | Steam turbine | Black Coal | 1983 | 660 | 44.1176 | 6 | 310 | 230 | 9.4488 | 38.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.7828%
Bayswater | BW02 | NSW | NCEN | Steam turbine | Black Coal | 1983 | 660 | 44.1176 | 6 | 310 | 230 | 9.4488 | 38.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.7828%
Bayswater | BW03 | NSW | NCEN | Steam turbine | Black Coal | 1983 | 660 | 44.1176 | 6 | 310 | 230 | 9.4488 | 38.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.7828%
Bayswater | BW04 | NSW | NCEN | Steam turbine | Black Coal | 1983 | 660 | 44.1176 | 6 | 310 | 230 | 9.4488 | 38.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.7828%
Liddell | LD01 | NSW | NCEN | Steam turbine | Black Coal | 1972 | 500 | 43.8095 | 5 | 240 | 180 | 10.1408 | 35.5 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8%
Liddell | LD02 | NSW | NCEN | Steam turbine | Black Coal | 1972 | 500 | 43.8095 | 5 | 240 | 180 | 10.1408 | 35.5 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8%
Liddell | LD03 | NSW | NCEN | Steam turbine | Black Coal | 1972 | 500 | 43.8095 | 5 | 240 | 180 | 10.1408 | 35.5 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8%
Liddell | LD04 | NSW | NCEN | Steam turbine | Black Coal | 1972 | 500 | 43.8095 | 5 | 240 | 180 | 10.1408 | 35.5 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8%
Tallawarra | TALWA1 | NSW | NCEN | CCGT | Natural gas | 2009 | 420 | 0 | 3 | 360 | 360 | 6.9903 | 51.5 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 1.429%
Blowering | BLOWERNG | NSW | SWNSW | Hydro | Hydro | 1969 | 80 | 6 | 1 | 120 | 120 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 2.5%
Hunter Valley | HVGTS1 | NSW | NCEN | OCGT | Distillate | 1988 | 25 | 0 | 1 | 60 | 60 | 12.7208 | 28.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4%
Hunter Valley | HVGTS2 | NSW | NCEN | OCGT | Distillate | 1988 | 25 | 0 | 1 | 60 | 60 | 12.7208 | 28.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4%
Barron Gorge | BARRON-1 | QLD | NQ | Hydro | Hydro | 1963 | 33 | 0 | 1 | 180 | 180 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 0 | 0 | 0 | 5 | 3 | 2 | 9.091%
Barron Gorge | BARRON-2 | QLD | NQ | Hydro | Hydro | 1963 | 33 | 0 | 1 | 180 | 180 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 0 | 0 | 0 | 5 | 3 | 2 | 9.091%
Kareeya | KAREEYA1 | QLD | NQ | Hydro | Hydro | 1958 | 21.6 | 25 | 1 | 300 | 120 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 0 | 0 | 0 | 5 | 3 | 2 | 23.15%
Kareeya | KAREEYA2 | QLD | NQ | Hydro | Hydro | 1958 | 21.6 | 25 | 1 | 300 | 120 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 0 | 0 | 0 | 5 | 3 | 2 | 23.15%
Kareeya | KAREEYA3 | QLD | NQ | Hydro | Hydro | 1958 | 21.6 | 25 | 1 | 300 | 120 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 0 | 0 | 0 | 5 | 3 | 2 | 23.15%
Kareeya | KAREEYA4 | QLD | NQ | Hydro | Hydro | 1958 | 21.6 | 25 | 1 | 300 | 120 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 0 | 0 | 0 | 5 | 3 | 2 | 23.15%
Wivenhoe | W/HOE#1 | QLD | SEQ | Hydro | Hydro | 1984 | 250 | 25 | 1 | 7200 | 7200 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 48%
Wivenhoe | W/HOE#2 | QLD | SEQ | Hydro | Hydro | 1984 | 250 | 25 | 1 | 7200 | 7200 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 48%
Bastyan | BASTYAN | TAS | TAS | Hydro | Hydro | 1983 | 79.9 | 0.07 | 1 | 1790 | 1790 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 37.34%
Cethana | CETHANA | TAS | TAS | Hydro | Hydro | 1971 | 85 | 0 | 1 | 1790 | 1790 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 35.1%
Devils Gate | DEVILS_G | TAS | TAS | Hydro | Hydro | 1969 | 60 | 8 | 1 | 1790 | 1790 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 49.72%
Fisher | FISHER | TAS | TAS | Hydro | Hydro | 1973 | 43.2 | 0 | 1 | 890 | 890 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 34.34%
Gordon | GO181-1 | TAS | TAS | Hydro | Hydro | 1978 | 144 | 0 | 1 | 5250 | 140 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 60.76%
Gordon | GO182-2 | TAS | TAS | Hydro | Hydro | 1978 | 144 | 0 | 1 | 5250 | 140 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 60.76%
Gordon | GO183-3 | TAS | TAS | Hydro | Hydro | 1978 | 144 | 0 | 1 | 5250 | 140 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 60.76%
John Butters | JBUTTERS | TAS | TAS | Hydro | Hydro | 1992 | 144 | 0 | 1 | 1730 | 1730 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 20.02%
Lake Echo | LK_ECHO | TAS | TAS | Hydro | Hydro | 1956 | 32.4 | 0 | 1 | 1000 | 1000 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 51.44%
Lemonthyme_Wilmot | LM111-1 | TAS | TAS | Hydro | Hydro | 1970 | 51 | 0 | 1 | 1170 | 1170 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 38.24%
Lemonthyme_Wilmot | WI111-1 | TAS | TAS | Hydro | Hydro | 1970 | 30.6 | 0 | 1 | 1170 | 1170 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 63.73%
Liapootah_Wayatinah_Catagunya | CA111-1 | TAS | TAS | Hydro | Hydro | 1960 | 24 | 0 | 1 | 2480 | 2480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 172.2%
Liapootah_Wayatinah_Catagunya | CA112-2 | TAS | TAS | Hydro | Hydro | 1960 | 24 | 0 | 1 | 2480 | 2480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 172.2%
Liapootah_Wayatinah_Catagunya | LI111-1 | TAS | TAS | Hydro | Hydro | 1960 | 27.9 | 0 | 1 | 2480 | 2480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 148.1%
Liapootah_Wayatinah_Catagunya | LI112-2 | TAS | TAS | Hydro | Hydro | 1960 | 27.9 | 0 | 1 | 2480 | 2480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 148.1%
Liapootah_Wayatinah_Catagunya | LI113-3 | TAS | TAS | Hydro | Hydro | 1960 | 27.9 | 0 | 1 | 2480 | 2480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 148.1%
Liapootah_Wayatinah_Catagunya | WY111-1 | TAS | TAS | Hydro | Hydro | 1960 | 12.8 | 0 | 1 | 2480 | 2480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 322.9%
Liapootah_Wayatinah_Catagunya | WY111-2 | TAS | TAS | Hydro | Hydro | 1960 | 12.8 | 0 | 1 | 2480 | 2480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 322.9%
Liapootah_Wayatinah_Catagunya | WY111-3 | TAS | TAS | Hydro | Hydro | 1960 | 12.8 | 0 | 1 | 2480 | 2480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 322.9%
Mackintosh | MACKNTSH | TAS | TAS | Hydro | Hydro | 1982 | 79.9 | 0 | 1 | 1800 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 37.55%
Meadowbank | MEADOWBK | TAS | TAS | Hydro | Hydro | 1967 | 40 | 0 | 1 | 480 | 480 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 20%
Poatina | PO161-1 | TAS | TAS | Hydro | Hydro | 1964 | 50 | 0 | 1 | 2250 | 2260 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 75.33%
Poatina | PO162-2 | TAS | TAS | Hydro | Hydro | 1964 | 50 | 0 | 1 | 2250 | 2260 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 75.33%
Poatina | PO163-3 | TAS | TAS | Hydro | Hydro | 1964 | 50 | 0 | 1 | 2250 | 2260 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 75.33%
Poatina | PO164-4 | TAS | TAS | Hydro | Hydro | 1964 | 50 | 0 | 1 | 2250 | 2260 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 75.33%
Poatina | PO165-5 | TAS | TAS | Hydro | Hydro | 1964 | 50 | 0 | 1 | 2250 | 2260 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 75.33%
Poatina | PO166-6 | TAS | TAS | Hydro | Hydro | 1964 | 50 | 0 | 1 | 2250 | 2260 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 75.33%
Reece | REECE1 | TAS | TAS | Hydro | Hydro | 1986 | 115.6 | 0 | 1 | 1800 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 25.95%
Reece | REECE2 | TAS | TAS | Hydro | Hydro | 1986 | 115.6 | 0 | 1 | 1800 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 25.95%
Tarraleah | TA111-1 | TAS | TAS | Hydro | Hydro | 1938 | 15 | 0 | 1 | 1000 | 1000 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 111.1%
Tarraleah | TA111-2 | TAS | TAS | Hydro | Hydro | 1938 | 15 | 0 | 1 | 1000 | 1000 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 111.1%
Tarraleah | TA111-3 | TAS | TAS | Hydro | Hydro | 1938 | 15 | 0 | 1 | 1000 | 1000 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 111.1%
Tarraleah | TA112-4 | TAS | TAS | Hydro | Hydro | 1938 | 15 | 0 | 1 | 1000 | 1000 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 111.1%
Tarraleah | TA112-5 | TAS | TAS | Hydro | Hydro | 1938 | 15 | 0 | 1 | 1000 | 1000 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 111.1%
Tarraleah | TA112-6 | TAS | TAS | Hydro | Hydro | 1938 | 15 | 0 | 1 | 1000 | 1000 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 111.1%
Trevallyn | TR111-1 | TAS | TAS | Hydro | Hydro | 1955 | 20 | 0 | 1 | 1710 | 1710 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 142.5%
Trevallyn | TR111-2 | TAS | TAS | Hydro | Hydro | 1955 | 20 | 0 | 1 | 1710 | 1710 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 142.5%
Trevallyn | TR112-3 | TAS | TAS | Hydro | Hydro | 1955 | 26.5 | 0 | 1 | 1710 | 1710 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 107.5%
Trevallyn | TR112-4 | TAS | TAS | Hydro | Hydro | 1955 | 26.5 | 0 | 1 | 1710 | 1710 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 107.5%
Tribute | TRIBUTE | TAS | TAS | Hydro | Hydro | 1994 | 82.8 | 0 | 1 | 1780 | 1780 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 35.83%
Tungatinah | TU111-1 | TAS | TAS | Hydro | Hydro | 1953 | 25 | 0 | 1 | 1930 | 1930 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 128.7%
Tungatinah | TU112-2 | TAS | TAS | Hydro | Hydro | 1953 | 25 | 0 | 1 | 1930 | 1930 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 128.7%
Tungatinah | TU113-3 | TAS | TAS | Hydro | Hydro | 1953 | 25 | 0 | 1 | 1930 | 1930 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 128.7%
Tungatinah | TU114-4 | TAS | TAS | Hydro | Hydro | 1953 | 25 | 0 | 1 | 1930 | 1930 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 128.7%
Tungatinah | TU115-5 | TAS | TAS | Hydro | Hydro | 1953 | 25 | 0 | 1 | 1930 | 1930 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 128.7%
Dartmouth | DARTM1 | VIC | NVIC | Hydro | Hydro | 1960 | 185 | 12 | 1 | 3120 | 3010 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 28.11%
Eildon | EILDON1 | VIC | NVIC | Hydro | Hydro | 1957 | 60 | 30 | 1 | 900 | 900 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 25%
Eildon | EILDON2 | VIC | NVIC | Hydro | Hydro | 1957 | 60 | 30 | 1 | 900 | 900 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 25%
Hume (VIC) | HUMEV | VIC | NVIC | Hydro | Hydro | 1957 | 58 | 14 | 1 | 180 | 180 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 2 | 1 | 1 | 5 | 3 | 2 | 5.172%
McKay Creek | BOGONG1 | VIC | NVIC | Hydro | Hydro | 1980 | 80 | 0 | 1 | 3600 | 3530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 75%
McKay Creek | BOGONG2 | VIC | NVIC | Hydro | Hydro | 1980 | 80 | 0 | 1 | 3600 | 3530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 75%
McKay Creek | MCKAY11 | VIC | NVIC | Hydro | Hydro | 1980 | 25 | 0 | 1 | 3600 | 3530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 240%
McKay Creek | MCKAY12 | VIC | NVIC | Hydro | Hydro | 1980 | 25 | 0 | 1 | 3600 | 3530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 240%
McKay Creek | MCKAY13 | VIC | NVIC | Hydro | Hydro | 1980 | 25 | 0 | 1 | 3600 | 3530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 240%
McKay Creek | MCKAY14 | VIC | NVIC | Hydro | Hydro | 1980 | 25 | 0 | 1 | 3600 | 3530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 240%
McKay Creek | MCKAY15 | VIC | NVIC | Hydro | Hydro | 1980 | 25 | 0 | 1 | 3600 | 3530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 240%
McKay Creek | MCKAY16 | VIC | NVIC | Hydro | Hydro | 1980 | 25 | 0 | 1 | 3600 | 3530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 240%
Murray 1 | MURRAY01 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY02 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY03 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY04 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY05 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY06 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY07 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY08 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY09 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 1 | MURRAY10 | VIC | NVIC | Hydro | Hydro | 1967 | 95 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 210.5%
Murray 2 | MURRAY11 | VIC | NVIC | Hydro | Hydro | 1969 | 138 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 144.9%
Murray 2 | MURRAY12 | VIC | NVIC | Hydro | Hydro | 1969 | 138 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 144.9%
Murray 2 | MURRAY13 | VIC | NVIC | Hydro | Hydro | 1969 | 138 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 144.9%
Murray 2 | MURRAY14 | VIC | NVIC | Hydro | Hydro | 1969 | 138 | 0 | 1 | 12000 | 2530 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 144.9%
West Kiewa | WKIEWA1 | VIC | NVIC | Hydro | Hydro | 1956 | 30 | 0 | 1 | 600 | 600 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 33.33%
West Kiewa | WKIEWA2 | VIC | NVIC | Hydro | Hydro | 1956 | 30 | 0 | 1 | 600 | 600 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 33.33%
Smithfield | SITHE04 | NSW | NCEN | Cogen | Natural gas | 1997 | 64 | 0 | 5 | 70 | 180 | 8.3527 | 43.1 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 4.688%
Hume (NSW) | HUMENSW | NSW | SWNSW | Hydro | Hydro | 1957 | 58 | 14 | 1 | 180 | 180 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 2 | 1 | 1 | 5 | 3 | 2 | 5.172%
Mackay | MACKAYGT | QLD | NQ | OCGT | Distillate | 1975 | 34 | 0 | 1 | 600 | 600 | 12.7208 | 28.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 29.41%
Mt Stuart | MSTUART1 | QLD | NQ | OCGT | Distillate | 1998 | 146 | 0 | 1 | 600 | 600 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.849%
Mt Stuart | MSTUART2 | QLD | NQ | OCGT | Distillate | 1998 | 146 | 0 | 1 | 600 | 600 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.849%
Mt Stuart | MSTUART3 | QLD | NQ | OCGT | Distillate | 1998 | 131.5 | 0 | 1 | 600 | 600 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.605%
Port Lincoln | POR01-1 | SA | NSA | OCGT | Distillate | 1999 | 25 | 0 | 8 | 180 | 180 | 12.8114 | 28.1 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 12%
Port Lincoln | POR01-2 | SA | NSA | OCGT | Distillate | 1999 | 25 | 0 | 8 | 180 | 180 | 12.8114 | 28.1 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 12%
Port Lincoln | POR01-3 | SA | NSA | OCGT | Distillate | 1999 | 23.5 | 0 | 8 | 180 | 180 | 12.8114 | 28.1 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 12.77%
Snuggery | SNUG1 | SA | SESA | OCGT | Distillate | 1997 | 21 | 0 | 3 | 180 | 180 | 13.4328 | 26.8 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 14.29%
Snuggery | SNUG2 | SA | SESA | OCGT | Distillate | 1997 | 21 | 0 | 3 | 180 | 180 | 13.4328 | 26.8 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 14.29%
Snuggery | SNUG3 | SA | SESA | OCGT | Distillate | 1997 | 21 | 0 | 3 | 180 | 180 | 13.4328 | 26.8 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 14.29%
Uranquinty | URANQ11 | NSW | SWNSW | OCGT | Natural gas | 2009 | 166 | 0 | 1 | 660 | 660 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.627%
Uranquinty | URANQ12 | NSW | SWNSW | OCGT | Natural gas | 2009 | 166 | 0 | 1 | 660 | 660 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.627%
Uranquinty | URANQ13 | NSW | SWNSW | OCGT | Natural gas | 2009 | 166 | 0 | 1 | 660 | 660 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.627%
Uranquinty | URANQ14 | NSW | SWNSW | OCGT | Natural gas | 2009 | 166 | 0 | 1 | 660 | 660 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.627%
Colongra GT | CG1 | NSW | NCEN | OCGT | Natural gas | 2009 | 181 | 0 | 1 | 720 | 720 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.63%
Colongra GT | CG2 | NSW | NCEN | OCGT | Natural gas | 2009 | 181 | 0 | 1 | 720 | 720 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.63%
Colongra GT | CG3 | NSW | NCEN | OCGT | Natural gas | 2009 | 181 | 0 | 1 | 720 | 720 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.63%
Colongra GT | CG4 | NSW | NCEN | OCGT | Natural gas | 2009 | 181 | 0 | 1 | 720 | 720 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.63%
Barcaldine | BARCALDN | QLD | CQ | OCGT | Natural gas | 1996 | 37 | 0 | 1 | 180 | 180 | 12.7208 | 28.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 8.108%
Braemar | BRAEMAR1 | QLD | SWQ | OCGT | Natural gas | 2006 | 168 | 0 | 1 | 460 | 460 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4.563%
Braemar | BRAEMAR2 | QLD | SWQ | OCGT | Natural gas | 2006 | 168 | 0 | 1 | 460 | 460 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4.563%
Braemar | BRAEMAR3 | QLD | SWQ | OCGT | Natural gas | 2006 | 168 | 0 | 1 | 460 | 460 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4.563%
Braemar 2 | BRAEMAR5 | QLD | SWQ | OCGT | Natural gas | 2009 | 173 | 0 | 1 | 660 | 660 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.358%
Braemar 2 | BRAEMAR6 | QLD | SWQ | OCGT | Natural gas | 2009 | 173 | 0 | 1 | 660 | 660 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.358%
Braemar 2 | BRAEMAR7 | QLD | SWQ | OCGT | Natural gas | 2009 | 173 | 0 | 1 | 660 | 660 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.358%
Oakey | OAKEY1 | QLD | SWQ | OCGT | Natural gas | 2000 | 140.9 | 0 | 1 | 660 | 660 | 10.9422 | 32.9 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.807%
Oakey | OAKEY2 | QLD | SWQ | OCGT | Natural gas | 2000 | 140.9 | 0 | 1 | 660 | 660 | 10.9422 | 32.9 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.807%
Roma | ROMA_7 | QLD | SWQ | OCGT | Natural gas | 1999 | 40 | 0 | 1 | 480 | 480 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20%
Roma | ROMA_8 | QLD | SWQ | OCGT | Natural gas | 1999 | 40 | 0 | 1 | 480 | 480 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20%
Dry Creek | DRYCGT1 | SA | ADE | OCGT | Natural gas | 1973 | 52 | 0 | 1 | 300 | 300 | 13.6882 | 26.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 9.615%
Dry Creek | DRYCGT2 | SA | ADE | OCGT | Natural gas | 1973 | 52 | 0 | 1 | 300 | 300 | 13.6882 | 26.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 9.615%
Dry Creek | DRYCGT3 | SA | ADE | OCGT | Natural gas | 1973 | 52 | 0 | 1 | 300 | 300 | 13.6882 | 26.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 9.615%
Hallett | AGLHAL01 | SA | NSA | OCGT | Natural gas | 2002 | 17 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 58.82%
Hallett | AGLHAL02 | SA | NSA | OCGT | Natural gas | 2002 | 17 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 58.82%
Hallett | AGLHAL03 | SA | NSA | OCGT | Natural gas | 2002 | 17 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 58.82%
Hallett | AGLHAL04 | SA | NSA | OCGT | Natural gas | 2002 | 17.3 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 57.8%
Hallett | AGLHAL05 | SA | NSA | OCGT | Natural gas | 2002 | 17.3 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 57.8%
Hallett | AGLHAL06 | SA | NSA | OCGT | Natural gas | 2002 | 16.4 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 60.98%
Hallett | AGLHAL07 | SA | NSA | OCGT | Natural gas | 2002 | 24.8 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 40.32%
Hallett | AGLHAL08 | SA | NSA | OCGT | Natural gas | 2002 | 27.5 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 36.36%
Hallett | AGLHAL09 | SA | NSA | OCGT | Natural gas | 2002 | 24.8 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 40.32%
Hallett | AGLHAL10 | SA | NSA | OCGT | Natural gas | 2002 | 16.4 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 60.98%
Hallett | AGLHAL11 | SA | NSA | OCGT | Natural gas | 2002 | 16.4 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 60.98%
Hallett | AGLHAL12 | SA | NSA | OCGT | Natural gas | 2002 | 16.4 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 60.98%
Ladbroke Grove | LADBROK1 | SA | SESA | OCGT | Natural gas | 2000 | 40 | 0 | 1 | 480 | 480 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20%
Ladbroke Grove | LADBROK2 | SA | SESA | OCGT | Natural gas | 2000 | 40 | 0 | 1 | 480 | 480 | 11.8812 | 30.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20%
Mintaro | MINTARO | SA | NSA | OCGT | Natural gas | 1984 | 90 | 0 | 1 | 300 | 300 | 12.7208 | 28.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 5.556%
Quarantine | QPS1 | SA | ADE | OCGT | Natural gas | 2002 | 24 | 0 | 5 | 600 | 600 | 10.7143 | 33.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 41.67%
Quarantine | QPS2 | SA | ADE | OCGT | Natural gas | 2002 | 24 | 0 | 5 | 600 | 600 | 10.7143 | 33.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 41.67%
Quarantine | QPS3 | SA | ADE | OCGT | Natural gas | 2002 | 24 | 0 | 5 | 600 | 600 | 10.7143 | 33.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 41.67%
Quarantine | QPS4 | SA | ADE | OCGT | Natural gas | 2002 | 24 | 0 | 5 | 600 | 600 | 10.7143 | 33.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 41.67%
Quarantine | QPS5 | SA | ADE | OCGT | Natural gas | 2002 | 128 | 0 | 5 | 600 | 600 | 10.7143 | 33.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.812%
Bell Bay Three | BBTHREE1 | TAS | TAS | OCGT | Natural gas | 2006 | 40 | 0 | 3 | 600 | 600 | 12.0401 | 29.9 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 25%
Bell Bay Three | BBTHREE2 | TAS | TAS | OCGT | Natural gas | 2006 | 40 | 0 | 3 | 600 | 600 | 12.0401 | 29.9 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 25%
Bell Bay Three | BBTHREE3 | TAS | TAS | OCGT | Natural gas | 2006 | 40 | 0 | 3 | 600 | 600 | 12.0401 | 29.9 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 25%
Tamar Valley OCGT | TVPP104 | TAS | TAS | OCGT | Natural gas | 2010 | 58 | 0 | 1 | 600 | 600 | 12.7208 | 28.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 17.24%
Bairnsdale | BDL01 | VIC | LV | OCGT | Natural gas | 2001 | 47 | 0 | 1 | 240 | 240 | 10.4956 | 34.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 8.511%
Bairnsdale | BDL02 | VIC | LV | OCGT | Natural gas | 2001 | 47 | 0 | 1 | 240 | 240 | 10.4956 | 34.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 8.511%
Jeeralang A | JLA01 | VIC | LV | OCGT | Natural gas | 1979 | 53 | 0 | 3 | 540 | 540 | 15.2542 | 23.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 16.98%
Jeeralang A | JLA02 | VIC | LV | OCGT | Natural gas | 1979 | 53 | 0 | 3 | 540 | 540 | 15.2542 | 23.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 16.98%
Jeeralang A | JLA03 | VIC | LV | OCGT | Natural gas | 1979 | 53 | 0 | 3 | 540 | 540 | 15.2542 | 23.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 16.98%
Jeeralang A | JLA04 | VIC | LV | OCGT | Natural gas | 1979 | 53 | 0 | 3 | 540 | 540 | 15.2542 | 23.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 16.98%
Jeeralang B | JLB01 | VIC | LV | OCGT | Natural gas | 1980 | 76 | 0 | 3 | 360 | 360 | 15.2542 | 23.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.895%
Jeeralang B | JLB02 | VIC | LV | OCGT | Natural gas | 1980 | 76 | 0 | 3 | 360 | 360 | 15.2542 | 23.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.895%
Jeeralang B | JLB03 | VIC | LV | OCGT | Natural gas | 1980 | 76 | 0 | 3 | 360 | 360 | 15.2542 | 23.6 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.895%
Laverton North | Laverton North1 | VIC | MEL | OCGT | Natural gas | 2006 | 156 | 0 | 3 | 3330 | 680 | 11.5016 | 31.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 35.58%
Laverton North | Laverton North2 | VIC | MEL | OCGT | Natural gas | 2006 | 156 | 0 | 3 | 3330 | 680 | 11.5016 | 31.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 35.58%
Mortlake | MORTLK11 | VIC | MEL | OCGT | Natural gas | 2011 | 283 | 0 | 1 | 780 | 780 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4.594%
Mortlake | MORTLK12 | VIC | MEL | OCGT | Natural gas | 2011 | 283 | 0 | 1 | 780 | 780 | 11.1455 | 32.3 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4.594%
Somerton | AGLSOM01 | VIC | MEL | OCGT | Natural gas | 2002 | 40 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 25%
Somerton | AGLSOM02 | VIC | MEL | OCGT | Natural gas | 2002 | 40 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 25%
Somerton | AGLSOM03 | VIC | MEL | OCGT | Natural gas | 2002 | 40 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 25%
Somerton | AGLSOM04 | VIC | MEL | OCGT | Natural gas | 2002 | 40 | 0 | 1 | 600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 25%
Valley Power | VPGS1 | VIC | LV | OCGT | Natural gas | 2002 | 50 | 0 | 1 | 3600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 120%
Valley Power | VPGS2 | VIC | LV | OCGT | Natural gas | 2002 | 50 | 0 | 1 | 3600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 120%
Valley Power | VPGS3 | VIC | LV | OCGT | Natural gas | 2002 | 50 | 0 | 1 | 3600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 120%
Valley Power | VPGS4 | VIC | LV | OCGT | Natural gas | 2002 | 50 | 0 | 1 | 3600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 120%
Valley Power | VPGS5 | VIC | LV | OCGT | Natural gas | 2002 | 50 | 0 | 1 | 3600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 120%
Valley Power | VPGS6 | VIC | LV | OCGT | Natural gas | 2002 | 50 | 0 | 1 | 3600 | 600 | 14.876 | 24.2 | 5 | 5 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 120%
Smithfield | SITHE01 | NSW | NCEN | Cogen | Natural gas | 1997 | 38 | 0 | 5 | 70 | 180 | 8.3527 | 43.1 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 7.895%
Smithfield | SITHE02 | NSW | NCEN | Cogen | Natural gas | 1997 | 38 | 0 | 5 | 70 | 180 | 8.3527 | 43.1 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 7.895%
Smithfield | SITHE03 | NSW | NCEN | Cogen | Natural gas | 1997 | 38 | 0 | 5 | 70 | 180 | 8.3527 | 43.1 | 5 | 20 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 7.895%
Boco Rock Wind Farm | BOCORWF1 | NSW | CAN | Wind | Wind | 2015 | 113 | 0 | 1 | 630 | 620 | [6 empty] | 45.1 | 10.39 | 12 | 2 | 1 | 5 | 3 | 2 | 9.292%
Taralga Wind Farm | Taralga Wind Farm | NSW | NCEN | Wind | Wind | 2014 | 106.7 | 0 | 1 | 630 | 620 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 9.841%
Shoalhaven | SHGEN03 | NSW | NCEN | Hydro | Hydro | 1977 | 80 | 0 | 1 | 600 | 600 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 12.5%
Shoalhaven | SHGEN04 | NSW | NCEN | Hydro | Hydro | 1977 | 80 | 0 | 1 | 600 | 600 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 12.5%
Shoalhaven | SHGEN01 | NSW | NCEN | Hydro | Hydro | 1977 | 40 | 0 | 1 | 600 | 600 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 25%
Shoalhaven | SHGEN02 | NSW | NCEN | Hydro | Hydro | 1977 | 40 | 0 | 1 | 600 | 600 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 25%
Woodlawn Wind Farm | WOODLWN1 | NSW | CAN | Wind | Wind | 2011 | 48.3 | 0 | 1 | 900 | 180 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 31.06%
Guthega | GUTHEGA1 | NSW | CAN | Hydro | Hydro | 1955 | 30 | 35 | 1 | 590 | 600 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 33.33%
Guthega | GUTHEGA2 | NSW | CAN | Hydro | Hydro | 1955 | 30 | 35 | 1 | 590 | 600 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 33.33%
Gullen Range | GULLRWF1 | NSW | CAN | Wind | Wind | 2014 | 165.5 | 0 | 1 | 5000 | 5000 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 50.35%
Tumut 3 | TUMUT3_01 | NSW | SWNSW | Hydro | Hydro | 1973 | 250 | 0 | 1 | 12000 | 2120 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 80%
Tumut 3 | TUMUT3_02 | NSW | SWNSW | Hydro | Hydro | 1973 | 250 | 0 | 1 | 12000 | 2120 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 80%
Tumut 3 | TUMUT3_03 | NSW | SWNSW | Hydro | Hydro | 1973 | 250 | 0 | 1 | 12000 | 2120 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 80%
Callide B | CALL_B_1 | QLD | CQ | Steam turbine | Black Coal | 1989 | 350 | 49 | 9 | 190 | 190 | 9.1603 | 39.3 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.9048%
Callide B | CALL_B_2 | QLD | CQ | Steam turbine | Black Coal | 1989 | 350 | 49 | 9 | 190 | 190 | 9.1603 | 39.3 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.9048%
Callide Power Plant | CPP_3 | QLD | CQ | Steam turbine | Black Coal | 2001 | 450 | 49.3827 | 6 | 230 | 230 | 9.3023 | 38.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8519%
Callide Power Plant | CPP_4 | QLD | CQ | Steam turbine | Black Coal | 2001 | 450 | 49.3827 | 6 | 230 | 230 | 9.3023 | 38.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8519%
Gladstone | GSTONE1 | QLD | CQ | Steam turbine | Black Coal | 1980 | 280 | 39.2857 | 8 | 290 | 300 | 9.4737 | 38 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.786%
Gladstone | GSTONE2 | QLD | CQ | Steam turbine | Black Coal | 1980 | 280 | 39.2857 | 8 | 290 | 300 | 9.4737 | 38 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.786%
Gladstone | GSTONE3 | QLD | CQ | Steam turbine | Black Coal | 1980 | 280 | 39.2857 | 8 | 290 | 300 | 9.4737 | 38 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.786%
Gladstone | GSTONE4 | QLD | CQ | Steam turbine | Black Coal | 1980 | 280 | 39.2857 | 8 | 290 | 300 | 9.4737 | 38 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.786%
Gladstone | GSTONE5 | QLD | CQ | Steam turbine | Black Coal | 1980 | 280 | 39.2857 | 8 | 290 | 300 | 9.4737 | 38 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.786%
Gladstone | GSTONE6 | QLD | CQ | Steam turbine | Black Coal | 1980 | 280 | 39.2857 | 8 | 290 | 300 | 9.4737 | 38 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.786%
Kogan Creek | KPP_1 | QLD | SWQ | Steam turbine | Black Coal | 2007 | 750 | 46.6667 | 9 | 210 | 210 | 8.802 | 40.9 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.4667%
Millmerran | MPP_1 | QLD | SWQ | Steam turbine | Black Coal | 2002 | 426 | 40 | 6 | 60 | 60 | 9.2072 | 39.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.2347%
Millmerran | MPP_2 | QLD | SWQ | Steam turbine | Black Coal | 2002 | 426 | 40 | 6 | 60 | 60 | 9.2072 | 39.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.2347%
Stanwell | STAN-1 | QLD | CQ | Steam turbine | Black Coal | 1995 | 365 | 50 | 9 | 180 | 180 | 9.068 | 39.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8219%
Stanwell | STAN-2 | QLD | CQ | Steam turbine | Black Coal | 1995 | 365 | 50 | 9 | 180 | 180 | 9.068 | 39.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8219%
Stanwell | STAN-3 | QLD | CQ | Steam turbine | Black Coal | 1995 | 365 | 50 | 9 | 180 | 180 | 9.068 | 39.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8219%
Stanwell | STAN-4 | QLD | CQ | Steam turbine | Black Coal | 1995 | 365 | 50 | 9 | 180 | 180 | 9.068 | 39.7 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 0.8219%
Tarong | TARONG#1 | QLD | SWQ | Steam turbine | Black Coal | 1985 | 350 | 40 | 8 | 240 | 240 | 9.2072 | 39.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.143%
Tarong | TARONG#2 | QLD | SWQ | Steam turbine | Black Coal | 1985 | 350 | 40 | 8 | 240 | 240 | 9.2072 | 39.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.143%
Tarong | TARONG#3 | QLD | SWQ | Steam turbine | Black Coal | 1985 | 350 | 40 | 8 | 240 | 240 | 9.2072 | 39.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.143%
Tarong | TARONG#4 | QLD | SWQ | Steam turbine | Black Coal | 1985 | 350 | 40 | 8 | 240 | 240 | 9.2072 | 39.1 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.143%
Tarong North | TNPS1 | QLD | SWQ | Steam turbine | Black Coal | 2002 | 450 | 39.5034 | 6 | 320 | 320 | 8.6538 | 41.6 | 5 | 20 |  |  | 53.2 | 4.21 | 24 | 4 | 2 | 350 | 120 | 40 | 1.185%
Loy Yang A | LYA1 | VIC | LV | Steam turbine | Brown Coal | 1986 | 560 | 62 | 9 | 330 | 320 | 12.1622 | 29.6 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 0.9821%
Loy Yang A | LYA2 | VIC | LV | Steam turbine | Brown Coal | 1986 | 500 | 62 | 9 | 330 | 320 | 12.1622 | 29.6 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 1.1%
Loy Yang A | LYA3 | VIC | LV | Steam turbine | Brown Coal | 1986 | 560 | 62 | 9 | 330 | 320 | 12.1622 | 29.6 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 0.9821%
Loy Yang A | LYA4 | VIC | LV | Steam turbine | Brown Coal | 1986 | 560 | 62 | 9 | 330 | 320 | 12.1622 | 29.6 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 0.9821%
Loy Yang B | LOYYB1 | VIC | LV | Steam turbine | Brown Coal | 1995 | 500 | 60.9524 | 8 | 540 | 540 | 12.5436 | 28.7 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 1.8%
Loy Yang B | LOYYB2 | VIC | LV | Steam turbine | Brown Coal | 1995 | 500 | 60.9524 | 8 | 540 | 540 | 12.5436 | 28.7 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 1.8%
Yallourn | YWPS1 | VIC | LV | Steam turbine | Brown Coal | 1980 | 350 | 60 | 10 | 260 | 260 | 13.8996 | 25.9 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 1.238%
Yallourn | YWPS2 | VIC | LV | Steam turbine | Brown Coal | 1980 | 350 | 60 | 10 | 260 | 260 | 13.8996 | 25.9 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 1.238%
Yallourn | YWPS3 | VIC | LV | Steam turbine | Brown Coal | 1980 | 375 | 60 | 10 | 260 | 260 | 13.8996 | 25.9 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 1.156%
Yallourn | YWPS4 | VIC | LV | Steam turbine | Brown Coal | 1980 | 375 | 60 | 10 | 260 | 260 | 13.8996 | 25.9 | 5 | 20 |  |  | 53.2 | 4.21 | 48 | 4 | 2 | 350 | 120 | 40 | 1.156%
Torrens Island A | TORRA1 | SA | ADE | Steam turbine | Natural gas | 1967 | 120 | 0 | 5 | 290 | 300 | 11.4286 | 31.5 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 20 | 4 | 2 | 20 | 10 | 5 | 4.167%
Torrens Island A | TORRA2 | SA | ADE | Steam turbine | Natural gas | 1967 | 120 | 0 | 5 | 290 | 300 | 11.4286 | 31.5 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 20 | 4 | 2 | 20 | 10 | 5 | 4.167%
Torrens Island A | TORRA3 | SA | ADE | Steam turbine | Natural gas | 1967 | 120 | 0 | 5 | 290 | 300 | 11.4286 | 31.5 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 20 | 4 | 2 | 20 | 10 | 5 | 4.167%
Torrens Island A | TORRA4 | SA | ADE | Steam turbine | Natural gas | 1967 | 120 | 0 | 5 | 290 | 300 | 11.4286 | 31.5 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 20 | 4 | 2 | 20 | 10 | 5 | 4.167%
Torrens Island B | TORRB1 | SA | ADE | Steam turbine | Natural gas | 1977 | 200 | 0 | 5 | 450 | 300 | 10.7143 | 33.6 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 20 | 4 | 2 | 20 | 10 | 5 | 3.75%
Torrens Island B | TORRB2 | SA | ADE | Steam turbine | Natural gas | 1977 | 200 | 0 | 5 | 450 | 300 | 10.7143 | 33.6 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 20 | 4 | 2 | 20 | 10 | 5 | 3.75%
Torrens Island B | TORRB3 | SA | ADE | Steam turbine | Natural gas | 1977 | 200 | 0 | 5 | 450 | 300 | 10.7143 | 33.6 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 20 | 4 | 2 | 20 | 10 | 5 | 3.75%
Torrens Island B | TORRB4 | SA | ADE | Steam turbine | Natural gas | 1977 | 200 | 0 | 5 | 450 | 300 | 10.7143 | 33.6 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 20 | 4 | 2 | 20 | 10 | 5 | 3.75%
Newport | NPS | VIC | MEL | Steam turbine | Natural gas | 1980 | 510 | 0 | 5 | 420 | 420 | 10.2857 | 35 | 5 | 2.5 |  |  | 47.1277 | 2.3287 | 12 | 3 | 1 | 20 | 10 | 5 | 1.373%
Tumut 3 | TUMUT3_04 | NSW | SWNSW | Hydro | Hydro | 1973 | 250 | 0 | 1 | 12000 | 2120 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 80%
Tumut 3 | TUMUT3_05 | NSW | SWNSW | Hydro | Hydro | 1973 | 250 | 0 | 1 | 12000 | 2120 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 80%
Tumut 3 | TUMUT3_06 | NSW | SWNSW | Hydro | Hydro | 1973 | 250 | 0 | 1 | 12000 | 2120 | 3.6 | 100 |  |  | 1.7 |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 80%
Gunning | GUNNING1 | NSW | CAN | Wind | Wind | 2011 | 46.5 | 0 | 1 | 2820 | 2820 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 101.1%
Tumut 1 | TUMUT1_01 | NSW | SWNSW | Hydro | Hydro | 1959 | 82 | 0 | 1 | 7790 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 158.3%
Tumut 1 | TUMUT1_02 | NSW | SWNSW | Hydro | Hydro | 1959 | 82 | 0 | 1 | 7790 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 158.3%
Clements Gap Wind Farm | CLEMGPWF | SA | NSA | Wind | Wind | 2010 | 56.7 | 0 | 1 | 1790 | 1790 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 52.62%
Hallett 1 Wind Farm | HALLWF1 | SA | NSA | Wind | Wind | 2007 | 95 | 0 | 1 | 180 | 180 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 3.158%
Hallett 2 Wind Farm | HALLWF2 | SA | NSA | Wind | Wind | 2009 | 71 | 0 | 1 | 120 | 120 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 2.817%
Hallett 4 Wind Farm | NBHWF1 | SA | NSA | Wind | Wind | 2011 | 132 | 0 | 1 | 180 | 180 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 2.273%
Hallett 5 Wind Farm | BLUFF1 | SA | NSA | Wind | Wind | 2012 | 53 | 0 | 1 | 120 | 120 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 3.774%
Lake Bonney 2 Wind Farm | LKBONNY2 | SA | SESA | Wind | Wind | 2008 | 159 | 0 | 1 | 780 | 780 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 8.176%
Lake Bonney 3 Wind Farm | LKBONNY3 | SA | SESA | Wind | Wind | 2011 | 39 | 0 | 1 | 900 | 180 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 38.46%
Snowtown 2 North | SNOWNTH1 | SA | ADE | Wind | Wind | 2014 | 144 | 0 | 1 | 630 | 620 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 7.292%
Snowtown 2 South | SNOWSTH1 | SA | ADE | Wind | Wind | 2014 | 126 | 0 | 1 | 630 | 620 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 8.333%
Snowtown Wind Farm | SNOWTWN1 | SA | NSA | Wind | Wind | 2008 | 98.7 | 0 | 1 | 600 | 600 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 10.13%
Waterloo | WATERLWF | SA | NSA | Wind | Wind | 2011 | 120.8 | 0 | 1 | 1580 | 1580 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 21.8%
Musselroe Wind Farm | MUSSELR1 | TAS | TAS | Wind | Wind | 2012 | 168 | 0 | 1 | 10080 | 10080 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 100%
Macarthur | MACARTH1 | VIC | CVIC | Wind | Wind | 2012 | 420 | 0 | 1 | 560 | 560 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 2.222%
Mt Mercer | MERCER1 | VIC | CVIC | Wind | Wind | 2014 | 131.2 | 0 | 1 | 630 | 620 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 8.003%
Oaklands Hill | OAKLAND1 | VIC | CVIC | Wind | Wind | 2011 | 67.2 | 0 | 1 | 630 | 620 | [6 empty] | 45.1 | 10.39 | 0 | 0 | 0 | 5 | 3 | 2 | 15.62%
Tumut 1 | TUMUT1_03 | NSW | SWNSW | Hydro | Hydro | 1959 | 82 | 0 | 1 | 7790 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 158.3%
Tumut 1 | TUMUT1_04 | NSW | SWNSW | Hydro | Hydro | 1959 | 82 | 0 | 1 | 7790 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 158.3%
Tumut 2 | TUMUT2_01 | NSW | SWNSW | Hydro | Hydro | 1962 | 72 | 0 | 1 | 7790 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 180.3%
Tumut 2 | TUMUT2_02 | NSW | SWNSW | Hydro | Hydro | 1962 | 72 | 0 | 1 | 7790 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 180.3%
Tumut 2 | TUMUT2_03 | NSW | SWNSW | Hydro | Hydro | 1962 | 72 | 0 | 1 | 7790 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 180.3%
Tumut 2 | TUMUT2_04 | NSW | SWNSW | Hydro | Hydro | 1962 | 72 | 0 | 1 | 7790 | 1800 | 3.6 | 100 |  |  |  |  | 58.25 | 7.19 | 12 | 2 | 1 | 5 | 3 | 2 | 180.3%
Angaston | ANGAS1 | SA |  | OCGT | Distillate | 2006 | 30 | 0 | 2.5 | 490 | 490 | 12.775 | 28.18 |  | 6 |  |  | 15.12 | 11.18 | [6 empty] | 27.22%
Angaston | ANGAS2 | SA |  | OCGT | Distillate | 2006 | 20 | 0 | 2.5 | 330 | 330 | 12.775 | 28.18 |  | 6 |  |  | 15.12 | 11.18 | [6 empty] | 27.5%
Hornsdale Wind Farm Stage 1 | Hornsdale | SA |  | Wind | Wind | 2016 | 102 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Hornsdale Wind Farm Stage 2 | Hornsdale_Stage2_WF | SA |  | Wind | Wind | 2017 | 102 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Hornsdale Wind Farm Stage 3 | Hornsdale_Stage3_WF | SA |  | Wind | Wind | 2017 | 109 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Lonsdale | Lonsdale | SA |  | Reciprocating Engine | Distillate | 2011 | 21 | 0 | 2.5 | 230 | 230 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 18.25%
Port Stanvac 1 | PTSTAN1 | SA |  | Reciprocating Engine | Distillate | 2011 | 58 | 0 | 2.5 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 18.39%
Barker Inlet Power Station | Barker Inlet 1 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 2 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 3 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 4 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 5 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 6 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 7 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 8 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 9 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 10 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 11 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Barker Inlet Power Station | Barker Inlet 12 | SA | 2019 | Reciprocating Engine | Natural Gas | 2019 | 12 | 0 | 3 | 640 | 640 | 7.8947 | 45.6 |  | 6 |  |  | 15.12 | 11.18 | 6 | 1 | 1 | 100 | 100 | 100 | 88.89%
Canunda | CNUNDAWF | SA |  | Wind | Wind | 2005 | 46 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Cathedral Rocks | CATHROCK | SA |  | Wind | Wind | 2007 | 66 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Lake Bonney 1 Wind Farm | LKBONNY1 | SA |  | Wind | Wind | 2005 | 80.5 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Mt Millar | MTMILLAR | SA |  | Wind | Wind | 2006 | 70 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Starfish Hill | STARHLWF | SA |  | Wind | Wind | 2003 | 34.5 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Wattle Point | WPWF | SA |  | Wind | Wind | 2005 | 90.8 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Ararat | ARARATWF | VIC |  | Wind | Wind | 2017 | 240 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Bald Hills p1 | Bald Hills p1 | VIC |  | Wind | Wind | 2015 | 106.6 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Crowlands Wind Farm | CROWLANDSWF | VIC |  | Wind | Wind | 2020 | 80 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Challicum Hills | CHALLHWF | VIC |  | Wind | Wind | 2003 | 52.5 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Mortons Lane WF | Mortons Lane WF | VIC |  | Wind | Wind | 2012 | 19.5 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Yambuk | YAMBUKWF | VIC |  | Wind | Wind | 2010 | 30 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Portland Wind Farm | PORTWF | VIC |  | Wind | Wind | 2010 | 179 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Waubra | WAUBRAWF | VIC |  | Wind | Wind | 2009 | 192 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Woolnorth Studland Bay / Bluff Point | WOOLNTH1 | TAS |  | Wind | Wind | 2002, 2004, 2007 | 140 | 0 | 1 | [8 empty] | 45.1 | 10.39 | [6 empty] | 0%
Hornsdale Power Reserve Unit 1 | HPR | SA |  | Batteries |  | 2017 | 100 | 0 | [17 empty] | 0%
Channel Island | GT1 | NT |  | OCGT | Natural Gas/Distillate | 1986 | 31 | 0 | 3 | 509.64 | 509.64 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Channel Island | GT2 | NT |  | OCGT | Natural Gas/Distillate | 1986 | 31 | 0 | 3 | 509.64 | 509.64 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Channel Island | GT3 | NT |  | OCGT | Natural Gas/Distillate | 1987 | 31 | 0 | 3 | 509.64 | 509.64 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Channel Island | GT4 | NT |  | CCGT | Natural Gas/Distillate | 1987 | 31 | 0 | 5 | 79.98 | 79.98 | 12.775 | 28.18 |  | 6 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 4.3%
Channel Island | GT5 | NT |  | CCGT | Natural Gas/Distillate | 1987 | 31 | 0 | 5 | 79.98 | 79.98 | 7.4596 | 48.26 |  | 8 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 4.3%
Channel Island | ST1 | NT |  | CCGT/STG |  | 1987 | 31 | 0 | 5 | 79.98 | 79.98 | 7.4596 | 48.26 |  | 8 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 4.3%
Channel Island | GT7 | NT |  | OCGT | Natural Gas | 1989 | 42 | 0 | 3 | 690.48 | 690.48 | 7.4596 | 48.26 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Channel Island | GT8 | NT |  | OCGT | Natural Gas | 2011 | 45 | 0 | 3 | 739.8 | 739.8 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Channel Island | GT9 | NT |  | OCGT | Natural Gas | 2012 | 45 | 0 | 3 | 739.8 | 739.8 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Weddell | 1 | NT |  | OCGT | Natural Gas | 2008 | 43 | 0 | 3 | 706.92 | 706.92 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Weddell | 2 | NT |  | OCGT | Natural Gas | 2008 | 43 | 0 | 3 | 706.92 | 706.92 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Weddell | 3 | NT |  | OCGT | Natural Gas | 2014 | 43 | 0 | 3 | 706.92 | 706.92 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Katherine | 1 | NT |  | OCGT | Natural Gas/Distillate | 1991 | 8 | 0 | 3 | 131.52 | 131.52 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Katherine | 2 | NT |  | OCGT | Natural Gas/Distillate | 1993 | 8 | 0 | 3 | 131.52 | 131.52 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Katherine | 3 | NT |  | OCGT | Natural Gas/Distillate | 1994 | 8 | 0 | 3 | 131.52 | 131.52 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Katherine | 4 | NT |  | OCGT | Natural Gas/Distillate | 2012 | 12.5 | 0 | 3 | 205.5 | 205.5 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
LMS Generation | 1 | NT |  | Recip | Landfill gas |  | 1.1 | 0 | 3 | 12.21 | 12.21 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Pine Creek | 1 | NT |  | CCGT | Natural Gas | 1996 | 9 | 0 | 5 | 147.96 | 147.96 | 7.4596 | 48.26 |  | 8 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 27.4%
Pine Creek | 2 | NT |  | CCGT | Natural Gas | 1996 | 9 | 0 | 5 | 147.96 | 147.96 | 7.4596 | 48.26 |  | 8 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 27.4%
Pine Creek | 3 | NT |  | CCGT ST | Natural Gas | 1996 | 9 | 0 | 5 | 147.96 | 147.96 | 7.4596 | 48.26 |  | 8 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 27.4%
Pine Creek | 4 | NT |  | OCGT | Natural Gas/Distillate | 1989 | 4 | 0 | 3 | 65.76 | 65.76 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Pine Creek | 5 | NT |  | OCGT | Natural Gas/Distillate | 1989 | 4 | 0 | 3 | 65.76 | 65.76 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Pine Creek |  |  |  | OCGT | Natural Gas/Distillate | 1989 | 4 | 0 | 3 | 65.76 | 65.76 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Pine Creek |  |  |  | OCGT | Natural Gas/Distillate | 1995 | 10 | 0 | 3 | 164.4 | 164.4 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Owen Springs | 1 | NT |  | OCGT | Natural Gas/Distillate | 2009 | 3.9 | 0 | 3 | 26.91 | 26.91 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 11.5%
Owen Springs | 2 | NT |  | Recip | Natural Gas/Distillate | 2011 | 10.7 | 0 | 3 | 118.77 | 118.77 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 3 | NT |  | Recip | Natural Gas/Distillate | 2011 | 10.7 | 0 | 3 | 118.77 | 118.77 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 4 | NT |  | Recip | Natural Gas/Distillate | 2011 | 10.7 | 0 | 3 | 118.77 | 118.77 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 5 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 6 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 7 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 8 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 9 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 10 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 11 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 12 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 13 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Owen Springs | 14 | NT |  | Recip | Natural Gas/Distillate | 2017 | 4.1 | 0 | 3 | 45.51 | 45.51 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Brewer | 1 | NT |  | Recip | Natural gas | 2000 | 2.1 | 0 | 3 | 23.31 | 23.31 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Brewer | 2 | NT |  | Recip | Natural gas | 2000 | 2.1 | 0 | 3 | 23.31 | 23.31 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Brewer | 3 | NT |  | Recip | Natural gas | 2000 | 2.1 | 0 | 3 | 23.31 | 23.31 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Brewer | 4 | NT |  | Recip | Natural gas | 2000 | 2.1 | 0 | 3 | 23.31 | 23.31 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Crown Plaza Alice Springs | 1 | NT |  | Solar | Solar | 2009 | 0.3 |  |  | 3.33 | 3.33 | [8 empty] | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 1 | NT |  | Recip | Distillate | 1975 | 1.3 | 0 | 3 | 14.43 | 14.43 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 2 | NT |  | Recip | Distillate | 1975 | 1.3 | 0 | 3 | 14.43 | 14.43 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 3 | NT |  | Recip | Distillate | 1975 | 1.3 | 0 | 3 | 14.43 | 14.43 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 4 | NT |  | Recip | Distillate | 1978 | 1.3 | 0 | 3 | 14.43 | 14.43 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 5 | NT |  | Recip | Distillate | 1981 | 1.3 | 0 | 3 | 14.43 | 14.43 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 16 | NT |  | Recip | Distillate | 2008 | 1.3 | 0 | 3 | 14.43 | 14.43 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 17 | NT |  | Recip | Distillate | 2010 | 1.3 | 0 | 3 | 14.43 | 14.43 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 10 | NT |  | Recip | Natural gas | 1999 | 0.96 | 0 | 3 | 10.656 | 10.656 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 11 | NT |  | Recip | Natural gas | 1999 | 0.96 | 0 | 3 | 10.656 | 10.656 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 12 | NT |  | Recip | Natural gas | 1999 | 0.96 | 0 | 3 | 10.656 | 10.656 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 13 | NT |  | Recip | Natural gas | 1999 | 0.96 | 0 | 3 | 10.656 | 10.656 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 14 | NT |  | Recip | Natural gas | 1999 | 0.96 | 0 | 3 | 10.656 | 10.656 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek | 15 | NT |  | OCGT | Natural Gas/Distillate | 2004 | 3.9 | 0 | 3 | 64.116 | 64.116 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 27.4%
Tennant Creek |  | NT |  | Recip | Gas | 2017 | 2 | 0 | 3 | 22.2 | 22.2 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek |  | NT |  | Recip | Gas | 2017 | 2 | 0 | 3 | 22.2 | 22.2 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek |  | NT |  | Recip | Gas | 2017 | 2 | 0 | 3 | 22.2 | 22.2 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tennant Creek |  | NT |  | Recip | Distillate | 2018 | 1.5 | 0 | 3 | 16.65 | 16.65 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Yulara | 1 | NT |  | Recip | Distillate | 1982 | 0.7 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 290.7%
Yulara | 2 | NT |  | Recip | Distillate | 1982 | 0.7 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 290.7%
Yulara | 3 | NT |  | Recip | Distillate | 2006 | 1.5 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 135.7%
Yulara | 4 | NT |  | Recip | Distillate | 2006 | 1.5 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 135.7%
Yulara | 5 | NT |  | Recip | Natural Gas/Distillate | 1986 | 1.3 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 156.5%
Yulara | 6 | NT |  | Recip | Natural Gas/Distillate | 1986 | 1.3 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 156.5%
Yulara | 7 | NT |  | Recip | Distillate | 1987 | 0.8 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 254.4%
Yulara | 8 | NT |  | Recip | Distillate | 1987 | 0.8 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 254.4%
Yulara | 9 | NT |  | Recip | Distillate | 1987 | 0.8 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 254.4%
Yulara | 10 | NT |  | Recip | Natural Gas | 2000 | 0.9 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 226.1%
Yulara | 11 | NT |  | Recip | Natural Gas | 2000 | 0.9 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 226.1%
Yulara | 12 | NT |  | Recip | Natural Gas | 2000 | 0.9 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 226.1%
Yulara | 13 | NT |  | Recip | Natural Gas | 2000 | 0.9 | 0 | 3 | 122.1 | 122.1 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 226.1%
Kings Canyon |  | NT |  | Recip | Distillate | 2003 | 0.3 | 0 | 3 | 13.32 | 13.32 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 74%
Kings Canyon |  | NT |  | Recip | Distillate | 2003 | 0.3 | 0 | 3 | 13.32 | 13.32 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 74%
Kings Canyon |  | NT |  | Recip | Distillate | 2004 | 0.5 | 0 | 3 | 13.32 | 13.32 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 44.4%
Kings Canyon |  | NT |  | Solar | Solar | 2003 | 0.2 | 0 | 3 | 13.32 | 13.32 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 111%
Albany Wind Farm | ALBANY_WF1 | WA |  | Wind | Wind | 2001 | 21.6 |  |  | 0 | 0 | [14 empty] | 0%
Alcoa Wagerup | ALCOA_WGP | WA |  | Reciprocating Engine | Natural Gas | 1985 | 26 | 0 | 3 | 180 | 180 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 11.54%
Atlas | ATLAS | WA |  | Recip | landfill gas | 2006 |  | 0 | 3 | 0 | 0 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | #DIV/0!
Bluewaters 1 | BW1_BLUEWATERS_G2 | WA |  | Steam turbine | bituminous | 2008 | 217 | 40 | 6 | 182.28 | 182.28 | 10.1408 | 35.5 |  | 26 |  |  | 47.3 | 3.63 | 24 | 4 | 2 | 350 | 120 | 40 | 1.4%
Bluewaters 2 | BW2_BLUEWATERS_G1 | WA |  | Steam turbine | bituminous | 2009 | 217 | 40 | 6 | 182.28 | 182.28 | 10.1408 | 35.5 |  | 26 |  |  | 47.3 | 3.63 | 24 | 4 | 2 | 350 | 120 | 40 | 1.4%
Bridgetown Biomass | BRIDGETOWN_BIOMASS_PLANT | WA |  | Steam turbine | biomass | 2009 | 40 | 40 | 6 | 33.6 | 33.6 | 10.1408 | 35.5 |  | 26 |  |  | 47.3 | 3.63 | 24 | 4 | 2 | 350 | 120 | 40 | 1.4%
Bremer Bay Wind Farm | BREMER_BAY_WF1 | WA |  | wind | wind | 2004 | 0.6 |  |  | 0 | 0 | [14 empty] | 0%
Clean Tech Biogas | BIOGAS01 | WA |  | Recip | landfill gas | 2015 | 2 | 0 | 3 | 0 | 0 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 0%
Cockburn | COCKBURN_CCG1 | WA |  | CCGT | Natural Gas | 2003 | 249.7 | 0 | 5 | 0 | 0 | 7.4596 | 48.26 |  | 8 |  |  | 10.5 | 7.37 | 15 | 3 | 1 | 25 | 15 | 5 | 0%
Collgar Wind Farm | INVESTEC_COLLGAR_WF1 | WA |  | wind | wind | 2011 | 206 |  |  | 0 | 0 | [14 empty] | 0%
Collie G1 | COLLIE_G1 | WA |  | Steam turbine | bituminous | 1999 | 318.3 | 40 | 6 | 240 | 240 | 10.1408 | 35.5 |  | 26 |  |  | 47.3 | 3.63 | 24 | 4 | 2 | 350 | 120 | 40 | 1.257%
Denmark Wind Farm | DCWL_DENMARK_WF1 | WA |  | wind | wind | 2013 | 1.44 |  |  | 0 | 0 | [14 empty] | 0%
Emu Downs Wind Farm | EDWFNAB_WF1 | WA |  | wind | wind | 2006 | 80 |  |  | 0 | 0 | [14 empty] | 0%
Goldfields | PRK_AG | WA |  | Recip | Dual Gas/Distillate | 1996 | 68 | 0 | 3 | 180 | 180 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 4.412%
Gosnells Landfill Gas | GOSNELLS | WA |  | Recip | landfill gas | 2004 | 2 | 0 | 3 | 22.2 | 22.2 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Grasmere Wind Farm | GRASMERE_WF1 | WA |  |  | wind | 2012 | 13.8 |  |  | 0 | 0 | [14 empty] | 0%
Greenough River Solar Farm | GREENOUGH_RIVER_PV1 | WA |  | solar | solar | 2012 | 10 |  |  | 0 | 0 | [14 empty] | 0%
Henderson Landfill Gas | HENDERSON_RENEWABLE_IG1 | WA |  | Recip | landfill gas | 2006 | 3 | 0 | 3 | 33.3 | 33.3 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Kalamunda | KALAMUNDA_SG | WA |  | Recip | Distillate | 2010 | 1.3 | 0 | 3 | 36 | 36 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 46.15%
Kalbarri Wind Farm | KALBARRI_WF1 | WA |  |  | wind | 2009 | 1.6 |  |  | 0 | 0 | [14 empty] | 0%
Karakin Wind Farm | BLAIRFOX_KARAKIN_WF1 | WA |  |  | wind | 2013 | 5 |  |  | 0 | 0 | [14 empty] | 0%
Kemerton 1 | KEMERTON_GT11 | WA |  | OCGT | Dual Gas/Distillate | 2005 | 154.7 | 0 | 3 | 900 | 900 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 9.696%
Kemerton 2 | KEMERTON_GT12 | WA |  | OCGT | Dual Gas/Distillate | 2005 | 154.7 | 0 | 3 | 900 | 900 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 9.696%
NewGen Kwinana | NEWGEN_KWINANA_CCG1 | WA |  | CCGT | Gas | 2008 | 335 | 0 | 3 | 360 | 360 | 7.4596 | 48.26 |  | 8 |  |  | 4.2 | 10.53 | 15 | 3 | 1 | 25 | 15 | 5 | 1.791%
Kwinana EG1 | PPP_KCP_EG1 | WA |  | OCGT | Natural Gas | 1996 | 85.7 | 0 | 3 | 60 | 60 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 1.167%
Kwinana Gas Turbine 1 | KWINANA_GT1 | WA |  | OCGT | Dual Gas/Distillate | 1972 | 20.2 | 0 | 3 | 1440 | 1440 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 118.8%
Kwinana Gas Turbine 2 | KWINANA_GT2 | WA |  | OCGT | Dual Gas/Distillate | 2011 | 103.2 | 0 | 3 | 1980 | 1980 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 31.98%
Kwinana Gas Turbine 3 | KWINANA_GT3 | WA |  | OCGT | Dual Gas/Distillate | 2011 | 103.2 | 0 | 3 | 1980 | 1980 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 31.98%
Merredin Gas Turbine 1 | NAMKKN_MERR_SG1 | WA |  | OCGT | Distillate | 2011 | 46.3 | 0 | 3 | 360 | 360 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 12.96%
Merredin Gas Turbine 2 | NAMKKN_MERR_SG2 | WA |  | OCGT | Distillate | 2011 | 46.3 | 0 | 3 | 360 | 360 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 12.96%
Mount Barker Wind Farm | SKYFRM_MTBARKER_WF1 | WA |  |  | wind | 2010 | 2.43 | [18 empty] | 0%
Muja 5 | MUJA_G5 | WA |  | Steam turbine | bituminous | 1981 | 195.8 | 40 | 6 | 240 | 240 | 10.1408 | 35.5 |  | 26 |  |  | 47.3 | 3.63 | 24 | 4 | 2 | 350 | 120 | 40 | 2.043%
Muja 6 | MUJA_G6 | WA |  | Steam turbine | bituminous | 1981 | 193.6 | 40 | 6 | 240 | 240 | 10.1408 | 35.5 |  | 26 |  |  | 47.3 | 3.63 | 24 | 4 | 2 | 350 | 120 | 40 | 2.066%
Muja 7 | MUJA_G7 | WA |  | Steam turbine | bituminous | 1986 | 212.6 | 40 | 6 | 240 | 240 | 10.1408 | 35.5 |  | 26 |  |  | 47.3 | 3.63 | 24 | 4 | 2 | 350 | 120 | 40 | 1.881%
Muja 8 | MUJA_G8 | WA |  | Steam turbine | bituminous | 1986 | 212.6 | 40 | 6 | 240 | 240 | 10.1408 | 35.5 |  | 26 |  |  | 47.3 | 3.63 | 24 | 4 | 2 | 350 | 120 | 40 | 1.881%
Mumbida Wind Farm | MWF_MUMBIDA_WF1 | WA |  |  | wind | 2013 | 55 | [18 empty] | 0%
Mungarra Gas Turbine 1 | MUNGARRA-GT1 | WA |  | OCGT | Natural Gas | 1991 | 39.5 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20.25%
Mungarra Gas Turbine 2 | MUNGARRA_GT2 | WA |  | OCGT | Natural Gas | 1991 | 39.5 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20.25%
Mungarra Gas Turbine 3 | MUNGARRA_GT3 | WA |  | OCGT | Natural Gas | 1991 | 38 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 21.05%
Neerabup Gas Turbine 1 | NEWGEN_NEERABUP_GT1 | WA |  | OCGT | Natural Gas | 2008 | 171 | 0 | 3 | 660 | 660 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.433%
Neerabup Gas Turbine 2 | NEWGEN_NEERABUP_GT2 | WA |  | OCGT | Natural Gas | 2008 | 171 | 0 | 3 | 660 | 660 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.433%
Pinjar Gas Turbine 1 | PINJAR_GT1 | WA |  | OCGT | Dual Gas/Distillate | 1990 | 38.5 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20.78%
Pinjar Gas Turbine 2 | PINJAR_GT2 | WA |  | OCGT | Dual Gas/Distillate | 1990 | 38.5 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20.78%
Pinjar Gas Turbine 3 | PINJAR_GT3 | WA |  | OCGT | Dual Gas/Distillate | 1990 | 39.3 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20.36%
Pinjar Gas Turbine 4 | PINJAR_GT4 | WA |  | OCGT | Dual Gas/Distillate | 1990 | 39.3 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20.36%
Pinjar Gas Turbine 5 | PINJAR_GT5 | WA |  | OCGT | Dual Gas/Distillate | 1990 | 39.3 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20.36%
Pinjar Gas Turbine 7 | PINJAR_GT7 | WA |  | OCGT | Dual Gas/Distillate | 1990 | 39.3 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 20.36%
Pinjar Gas Turbine 9 | PINJAR_GT9 | WA |  | OCGT | Natural Gas | 1996 | 118.2 | 0 | 3 | 600 | 600 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 8.46%
Pinjar Gas Turbine 10 | PINJAR_GT10 | WA |  | OCGT | Natural Gas | 1996 | 118.2 | 0 | 3 | 600 | 600 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 8.46%
Pinjar Gas Turbine 11 | PINJAR-_GT11 | WA |  | OCGT | Natural Gas | 1996 | 130 | 0 | 3 | 600 | 600 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.692%
Pinjarra 1 | ALCOA_PNJ_U1 | WA |  | OCGT | Natural Gas | 2005 | 143 | 0 | 3 | 564 | 564 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.573%
Pinjarra 2 | ALCOA_PNJ_U2 | WA |  | OCGT | Natural Gas | 2006 | 143 | 0 | 3 | 564 | 564 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 6.573%
Red Hill Landfill Gas and Power | RED_HILL | WA |  | Recip | landfill gas | 1993 | 3.64 | 0 | 3 | 40.404 | 40.404 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Rockingham | ROCKINGHAM | WA |  | Recip | landfill gas | 2003 | 4 | 0 | 3 | 44.4 | 44.4 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
South Cardup | SOUTH_CARDUP | WA |  | Recip | landfill gas | 2005 | 4.16 | 0 | 3 | 46.176 | 46.176 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tamala Park | TAMALA_PARK | WA |  | Recip | landfill gas | 2004 | 4.74 | 0 | 3 | 52.614 | 52.614 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 18.5%
Tesla Geraldton | TESLA_GERALDTON_G1 | WA |  | Recip | Distillate | 2012 | 9.9 | 0 | 3 | 120 | 120 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 20.2%
Tesla Kemerton | TESLA_KEMERTON_G1 | WA |  | Recip | Distillate | 2012 | 9.9 | 0 | 3 | 120 | 120 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 20.2%
Tesla Northam | TESLA_NORTHAM_G1 | WA |  | Recip | Distillate | 2012 | 9.9 | 0 | 3 | 120 | 120 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 20.2%
Tesla Picton | TESLA_PICTON_G1 | WA |  | Recip | Distillate | 2011 | 9.9 | 0 | 3 | 120 | 120 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 20.2%
Tiwest | TIWEST_COG1 | WA |  | OCGT | Natural Gas | 1990 | 42.1 | 0 | 3 | 180 | 180 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 7.126%
Wagerup Gas Turbine 1 | ALINTA_WGP_GT | WA |  | OCGT | Dual Gas/Distillate | 2007 | 194.45 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4.114%
Wagerup Gas Turbine 2 | ALINTA_WGP_U2 | WA |  | OCGT | Dual Gas/Distillate | 2007 | 196.85 | 0 | 3 | 480 | 480 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 4.064%
Walkaway Wind Farm | ALINTA_WWF | WA |  |  | Wind | 2005 | 89.1 | [18 empty] | 0%
West Hills Wind Farm | BLAIRFOX_WESTHILLS_WF3 | WA |  |  | Wind | 2013 | 5 | [18 empty] | 0%
West Kalgoorlie GT2 | WEST_KALGOORLIE_GT2 | WA |  | OCGT | Distillate | 1984 | 41.2 | 0 | 3 | 138 | 138 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 5.583%
West Kalgoorlie GT3 | WEST_KALGOORLIE_GT3 | WA |  | OCGT | Distillate | 1990 | 23.3 | 0 | 3 | 138 | 138 | 12.775 | 28.18 |  | 6 |  |  | 4.2 | 10.53 | 6 | 1 | 1 | 100 | 100 | 100 | 9.871%
Southern Cross | STHRNCRS_IL | WA |  | Recip | Distillate | 2003 | 23 | 0 | 3 | 180 | 180 | 7.8947 | 45.6 |  | 6 |  |  | 4.2 | 16.42 | 6 | 1 | 1 | 100 | 100 | 100 | 13.04%

## processed
TimeEnd | Coal | PV (Utility) | Wind | PV (Rooftop) | Gas | Demand
2020-12-26 17:30 | 0.59181 | 0.41662 | 0.31331 | 0.097197 | 1 | 7641.12
2020-12-26 18:00 | 0.62295 | 0.29145 | 0.3656 | 0.049498 | 1 | 7706.96
2020-12-26 18:30 | 0.63507 | 0.17004 | 0.43786 | 0.017094 | 1 | 7816.25
2020-12-26 19:00 | 0.64427 | 0.046833 | 0.48553 | 0.0030965 | 1 | 7729.91
2020-12-26 19:30 | 0.65049 | 0.0018518 | 0.515 | 0.00020547 | 1 | 7733.7
2020-12-26 20:00 | 0.65054 | 0 | 0.50521 | 0 | 1 | 7652.16
2020-12-26 20:30 | 0.64355 | 0 | 0.48924 | 0 | 1 | 7527.59
2020-12-26 21:00 | 0.63714 | 0 | 0.49188 | 0 | 1 | 7364.03
2020-12-26 21:30 | 0.62747 | 0 | 0.47645 | 0 | 1 | 7221.71
2020-12-26 22:00 | 0.60843 | 0 | 0.45258 | 0 | 1 | 6993.65
2020-12-26 22:30 | 0.60568 | 0 | 0.44332 | 0 | 1 | 6949.67
2020-12-26 23:00 | 0.58185 | 0 | 0.43996 | 0 | 1 | 6757.93
2020-12-26 23:30 | 0.55685 | 0 | 0.41445 | 0 | 1 | 6559.12
2020-12-27 | 0.52983 | 0 | 0.38731 | 0 | 1 | 6526.27
2020-12-27 00:30 | 0.48375 | 0 | 0.36536 | 0 | 1 | 6287.87
2020-12-27 01:00 | 0.4689 | 0 | 0.35877 | 0 | 1 | 6081.76
2020-12-27 01:30 | 0.44667 | 0 | 0.33334 | 0 | 1 | 5873.98
2020-12-27 02:00 | 0.40989 | 0 | 0.29718 | 0 | 1 | 5700.9
2020-12-27 02:30 | 0.39502 | 0 | 0.26229 | 0 | 1 | 5560.99
2020-12-27 03:00 | 0.38949 | 0 | 0.2386 | 0 | 1 | 5570.48
2020-12-27 03:30 | 0.37621 | 0 | 0.29683 | 0 | 1 | 5524.47
2020-12-27 04:00 | 0.3741 | 0 | 0.32436 | 6.1282e-05 | 1 | 5542.15
2020-12-27 04:30 | 0.37165 | 0 | 0.32293 | 0.0020295 | 1 | 5596.28
2020-12-27 05:00 | 0.37305 | 0.00061343 | 0.31121 | 0.018125 | 1 | 5642.57
2020-12-27 05:30 | 0.37187 | 0.029783 | 0.32924 | 0.056419 | 1 | 5784.42
2020-12-27 06:00 | 0.36685 | 0.14624 | 0.30335 | 0.11875 | 1 | 5995.96
2020-12-27 06:30 | 0.36127 | 0.29691 | 0.22789 | 0.20123 | 1 | 6304.43
2020-12-27 07:00 | 0.35298 | 0.4313 | 0.18299 | 0.30254 | 1 | 6682.04
2020-12-27 07:30 | 0.35868 | 0.50228 | 0.17484 | 0.41737 | 1 | 7165.72
2020-12-27 08:00 | 0.35052 | 0.53999 | 0.16739 | 0.52414 | 1 | 7434.29
2020-12-27 08:30 | 0.36182 | 0.56123 | 0.22096 | 0.60904 | 1 | 7821
2020-12-27 09:00 | 0.35519 | 0.59863 | 0.2258 | 0.68461 | 1 | 7949.38
2020-12-27 09:30 | 0.34771 | 0.6245 | 0.25457 | 0.7493 | 1 | 8075.45
2020-12-27 10:00 | 0.3434 | 0.61427 | 0.23513 | 0.80492 | 1 | 8179.02
2020-12-27 10:30 | 0.35661 | 0.61182 | 0.266 | 0.84252 | 1 | 8442.15
2020-12-27 11:00 | 0.3643 | 0.63623 | 0.24171 | 0.86628 | 1 | 8445.95
2020-12-27 11:30 | 0.36506 | 0.63374 | 0.21485 | 0.87364 | 1 | 8476.07
2020-12-27 12:00 | 0.36014 | 0.6311 | 0.20747 | 0.86391 | 1 | 8492.91
2020-12-27 12:30 | 0.36425 | 0.57998 | 0.24382 | 0.8507 | 1 | 8476.61
2020-12-27 13:00 | 0.37549 | 0.58653 | 0.25146 | 0.82698 | 1 | 8569.02
2020-12-27 13:30 | 0.38051 | 0.57132 | 0.27437 | 0.77651 | 1 | 8614.64
2020-12-27 14:00 | 0.38839 | 0.57152 | 0.30003 | 0.7256 | 1 | 8758.18
2020-12-27 14:30 | 0.39988 | 0.50769 | 0.33401 | 0.66873 | 1 | 8839.9
2020-12-27 15:00 | 0.41494 | 0.46301 | 0.31108 | 0.58769 | 1 | 8853.1
2020-12-27 15:30 | 0.44895 | 0.40436 | 0.34569 | 0.49876 | 1 | 8934.68
2020-12-27 16:00 | 0.4952 | 0.3489 | 0.35768 | 0.39072 | 1 | 9003
2020-12-27 16:30 | 0.55459 | 0.28061 | 0.36985 | 0.26688 | 1 | 8961.13
2020-12-27 17:00 | 0.61399 | 0.22065 | 0.37668 | 0.17159 | 1 | 9110.83
2020-12-27 17:30 | 0.63855 | 0.13703 | 0.35903 | 0.10785 | 1 | 8917.44
2020-12-27 18:00 | 0.67246 | 0.11108 | 0.29626 | 0.054433 | 1 | 8775.01
2020-12-27 18:30 | 0.68002 | 0.048696 | 0.27471 | 0.017992 | 1 | 8584.14
2020-12-27 19:00 | 0.67983 | 0.011248 | 0.27991 | 0.002664 | 1 | 8461.84
2020-12-27 19:30 | 0.67223 | 6.8796e-05 | 0.26668 | 0.00010454 | 1 | 8420.81
2020-12-27 20:00 | 0.67103 | 0 | 0.19961 | 0 | 1 | 8287.45
2020-12-27 20:30 | 0.64453 | 0 | 0.24637 | 0 | 1 | 8148.41
2020-12-27 21:00 | 0.60947 | 0 | 0.39349 | 0 | 1 | 7908.94
2020-12-27 21:30 | 0.60746 | 0 | 0.4639 | 0 | 1 | 7776.6
2020-12-27 22:00 | 0.58495 | 0 | 0.51538 | 0 | 1 | 7637.42
2020-12-27 22:30 | 0.56883 | 0 | 0.5358 | 0 | 1 | 7439.12
2020-12-27 23:00 | 0.52697 | 0 | 0.57818 | 0 | 1 | 7179.57
2020-12-27 23:30 | 0.50189 | 0 | 0.64293 | 0 | 1 | 6997.01
2020-12-28 | 0.47253 | 0 | 0.67605 | 0 | 1 | 6844.05
2020-12-28 00:30 | 0.44216 | 0 | 0.64469 | 0 | 1 | 6596.19
2020-12-28 01:00 | 0.42649 | 0 | 0.62951 | 0 | 1 | 6419.81
2020-12-28 01:30 | 0.40849 | 0 | 0.60743 | 0 | 1 | 6187.5
2020-12-28 02:00 | 0.39608 | 0 | 0.59614 | 0 | 1 | 6022.35
2020-12-28 02:30 | 0.39251 | 0 | 0.56535 | 0 | 1 | 5963.67
2020-12-28 03:00 | 0.38598 | 0 | 0.54786 | 0 | 1 | 5892.86
2020-12-28 03:30 | 0.38647 | 0 | 0.55699 | 0 | 1 | 5896.37
2020-12-28 04:00 | 0.38574 | 0 | 0.54018 | 1.8024e-05 | 1 | 5900.55
2020-12-28 04:30 | 0.39763 | 0 | 0.49836 | 0.0009733 | 1 | 5966.5
2020-12-28 05:00 | 0.41042 | 0 | 0.45246 | 0.010104 | 1 | 6046.92
2020-12-28 05:30 | 0.42343 | 0.0074529 | 0.4362 | 0.032923 | 1 | 6225.61
2020-12-28 06:00 | 0.40755 | 0.091745 | 0.42122 | 0.066617 | 1 | 6464.48
2020-12-28 06:30 | 0.37261 | 0.22246 | 0.39109 | 0.10955 | 1 | 6651.19
2020-12-28 07:00 | 0.36917 | 0.38935 | 0.43307 | 0.16244 | 1 | 6916.01
2020-12-28 07:30 | 0.37636 | 0.45785 | 0.50769 | 0.24863 | 1 | 7249.31
2020-12-28 08:00 | 0.3775 | 0.47601 | 0.53291 | 0.37033 | 1 | 7609.29
2020-12-28 08:30 | 0.37188 | 0.48729 | 0.51208 | 0.47516 | 1 | 7885.34
2020-12-28 09:00 | 0.37102 | 0.51998 | 0.48434 | 0.5743 | 1 | 8294.77
2020-12-28 09:30 | 0.37752 | 0.51856 | 0.46847 | 0.63416 | 1 | 8489.95
2020-12-28 10:00 | 0.37589 | 0.51296 | 0.49963 | 0.65867 | 1 | 8676.27
2020-12-28 10:30 | 0.37895 | 0.55673 | 0.51433 | 0.67053 | 1 | 8793.24
2020-12-28 11:00 | 0.37866 | 0.54883 | 0.51799 | 0.68968 | 1 | 8824.47
2020-12-28 11:30 | 0.39187 | 0.57588 | 0.49178 | 0.70216 | 1 | 8963.85
2020-12-28 12:00 | 0.39568 | 0.57721 | 0.53532 | 0.65772 | 1 | 8852.82
2020-12-28 12:30 | 0.40758 | 0.56229 | 0.55931 | 0.6046 | 1 | 8849.29
2020-12-28 13:00 | 0.41448 | 0.56363 | 0.50099 | 0.57815 | 1 | 8784.74
2020-12-28 13:30 | 0.41033 | 0.56443 | 0.4239 | 0.52604 | 1 | 8594.22
2020-12-28 14:00 | 0.41325 | 0.57745 | 0.47249 | 0.44647 | 1 | 8422.28
2020-12-28 14:30 | 0.42041 | 0.54435 | 0.48236 | 0.37786 | 1 | 8294.82
2020-12-28 15:00 | 0.43536 | 0.50426 | 0.52185 | 0.29963 | 1 | 8072.69
2020-12-28 15:30 | 0.46527 | 0.49206 | 0.47419 | 0.24391 | 1 | 8046.99
2020-12-28 16:00 | 0.52118 | 0.4648 | 0.48694 | 0.18815 | 1 | 8110.57
2020-12-28 16:30 | 0.5694 | 0.35105 | 0.52698 | 0.13899 | 1 | 8062.52
2020-12-28 17:00 | 0.60347 | 0.35674 | 0.54869 | 0.092889 | 1 | 8191.09
2020-12-28 17:30 | 0.59975 | 0.29853 | 0.48939 | 0.056098 | 1 | 8068.59
2020-12-28 18:00 | 0.58648 | 0.21774 | 0.50023 | 0.030371 | 1 | 7886.74
2020-12-28 18:30 | 0.58456 | 0.1134 | 0.47614 | 0.012534 | 1 | 7650.19
2020-12-28 19:00 | 0.60735 | 0.0334 | 0.45847 | 0.002563 | 1 | 7489.8
2020-12-28 19:30 | 0.61255 | 0.001181 | 0.47713 | 0.00018385 | 1 | 7458.45
2020-12-28 20:00 | 0.60834 | 0 | 0.48725 | 0 | 1 | 7344.74
2020-12-28 20:30 | 0.59455 | 0 | 0.44927 | 0 | 1 | 7214.79
2020-12-28 21:00 | 0.59282 | 0 | 0.41958 | 0 | 1 | 7127.49
2020-12-28 21:30 | 0.59884 | 0 | 0.39716 | 0 | 1 | 7114.83
2020-12-28 22:00 | 0.58479 | 0 | 0.37587 | 0 | 1 | 7038.47
2020-12-28 22:30 | 0.59487 | 0 | 0.36202 | 0 | 1 | 6988.93
2020-12-28 23:00 | 0.59994 | 0 | 0.37708 | 0 | 1 | 6892.61
2020-12-28 23:30 | 0.6023 | 0 | 0.41485 | 0 | 1 | 6871.67
2020-12-29 | 0.58357 | 0 | 0.41149 | 0 | 1 | 6726.15
2020-12-29 00:30 | 0.55653 | 0 | 0.39178 | 0 | 1 | 6528.22
2020-12-29 01:00 | 0.53662 | 0 | 0.35176 | 0 | 1 | 6325.13
2020-12-29 01:30 | 0.5062 | 0 | 0.29979 | 0 | 1 | 6060.34
2020-12-29 02:00 | 0.48028 | 0 | 0.29743 | 0 | 1 | 5872.49
2020-12-29 02:30 | 0.47243 | 0 | 0.25389 | 0 | 1 | 5791.26
2020-12-29 03:00 | 0.46224 | 0 | 0.22774 | 0 | 1 | 5699.32
2020-12-29 03:30 | 0.44992 | 0 | 0.2133 | 0 | 1 | 5676.79
2020-12-29 04:00 | 0.45948 | 0 | 0.18847 | 7.2096e-05 | 1 | 5689.15
2020-12-29 04:30 | 0.48086 | 0 | 0.24041 | 0.0015393 | 1 | 5851.74
2020-12-29 05:00 | 0.4931 | 0.00013186 | 0.23416 | 0.010353 | 1 | 5958.49
2020-12-29 05:30 | 0.51007 | 0.018059 | 0.23974 | 0.027087 | 1 | 6220.36
2020-12-29 06:00 | 0.50273 | 0.10914 | 0.23889 | 0.05019 | 1 | 6500.67
2020-12-29 06:30 | 0.48151 | 0.24929 | 0.23522 | 0.086508 | 1 | 6795.47
2020-12-29 07:00 | 0.4769 | 0.34814 | 0.2297 | 0.12992 | 1 | 7023.46
2020-12-29 07:30 | 0.45199 | 0.40701 | 0.24305 | 0.18004 | 1 | 7437.48
2020-12-29 08:00 | 0.43449 | 0.42504 | 0.26464 | 0.22935 | 1 | 7684.58
2020-12-29 08:30 | 0.46592 | 0.44096 | 0.27391 | 0.29478 | 1 | 7878.46
2020-12-29 09:00 | 0.4739 | 0.43789 | 0.27733 | 0.3408 | 1 | 7948.3
2020-12-29 09:30 | 0.48052 | 0.45123 | 0.27552 | 0.33945 | 1 | 7991.43
2020-12-29 10:00 | 0.4965 | 0.4736 | 0.29854 | 0.34606 | 1 | 8047.99
2020-12-29 10:30 | 0.51002 | 0.46246 | 0.27834 | 0.37862 | 1 | 8169.48
2020-12-29 11:00 | 0.4783 | 0.47904 | 0.24582 | 0.39407 | 1 | 8096.43
2020-12-29 11:30 | 0.45183 | 0.48979 | 0.21911 | 0.37259 | 1 | 8001.69
2020-12-29 12:00 | 0.47109 | 0.52167 | 0.21094 | 0.3546 | 1 | 8069.08
2020-12-29 12:30 | 0.46543 | 0.54407 | 0.22884 | 0.35859 | 1 | 8085.86
2020-12-29 13:00 | 0.44649 | 0.58939 | 0.22781 | 0.38885 | 1 | 8081.93
2020-12-29 13:30 | 0.43255 | 0.61917 | 0.25274 | 0.39427 | 1 | 8010.82
2020-12-29 14:00 | 0.43615 | 0.60446 | 0.2587 | 0.34708 | 1 | 7828.88
2020-12-29 14:30 | 0.46788 | 0.57279 | 0.27483 | 0.32244 | 1 | 7900.45
2020-12-29 15:00 | 0.48262 | 0.56698 | 0.28428 | 0.29997 | 1 | 7893.39
2020-12-29 15:30 | 0.4964 | 0.53717 | 0.31059 | 0.27117 | 1 | 7944.14
2020-12-29 16:00 | 0.52406 | 0.51145 | 0.32148 | 0.21196 | 1 | 7942.09
2020-12-29 16:30 | 0.54371 | 0.51361 | 0.32555 | 0.15953 | 1 | 7953.51
2020-12-29 17:00 | 0.55996 | 0.49891 | 0.34296 | 0.11212 | 1 | 8022.56
2020-12-29 17:30 | 0.57764 | 0.43219 | 0.34001 | 0.071011 | 1 | 7990.88
2020-12-29 18:00 | 0.59192 | 0.33787 | 0.37901 | 0.039292 | 1 | 7864.22
2020-12-29 18:30 | 0.59818 | 0.17897 | 0.44665 | 0.015429 | 1 | 7627.69
2020-12-29 19:00 | 0.62111 | 0.05088 | 0.4897 | 0.0030172 | 1 | 7551.32
2020-12-29 19:30 | 0.64514 | 0.0028378 | 0.54465 | 0.00021268 | 1 | 7591.41
2020-12-29 20:00 | 0.64956 | 0 | 0.57847 | 0 | 1 | 7602.6
2020-12-29 20:30 | 0.65673 | 0 | 0.58754 | 0 | 1 | 7689.1
2020-12-29 21:00 | 0.64442 | 0 | 0.59912 | 0 | 1 | 7580.68
2020-12-29 21:30 | 0.63677 | 0 | 0.65518 | 0 | 1 | 7586.93
2020-12-29 22:00 | 0.62155 | 0 | 0.66753 | 0 | 1 | 7449.95
2020-12-29 22:30 | 0.62858 | 0 | 0.65261 | 0 | 1 | 7499.3
2020-12-29 23:00 | 0.59899 | 0 | 0.66827 | 0 | 1 | 7226.35
2020-12-29 23:30 | 0.59763 | 0 | 0.67471 | 0 | 1 | 7216.69
2020-12-30 | 0.59021 | 0 | 0.65631 | 0 | 1 | 7113.21
2020-12-30 00:30 | 0.5721 | 0 | 0.62119 | 0 | 1 | 6875.53
2020-12-30 01:00 | 0.54047 | 0 | 0.61076 | 0 | 1 | 6563.12
2020-12-30 01:30 | 0.49336 | 0 | 0.60292 | 0 | 1 | 6272.39
2020-12-30 02:00 | 0.45616 | 0 | 0.58172 | 0 | 1 | 5995.15
2020-12-30 02:30 | 0.44454 | 0 | 0.58739 | 0 | 1 | 5911.45
2020-12-30 03:00 | 0.43393 | 0 | 0.60274 | 0 | 1 | 5840.87
2020-12-30 03:30 | 0.43084 | 0 | 0.59625 | 0 | 1 | 5804.33
2020-12-30 04:00 | 0.43329 | 0 | 0.59996 | 2.1629e-05 | 1 | 5815.2
2020-12-30 04:30 | 0.45569 | 0 | 0.59238 | 0.0010021 | 1 | 5938.4
2020-12-30 05:00 | 0.47707 | 0.00025799 | 0.55944 | 0.010306 | 1 | 6064
2020-12-30 05:30 | 0.49773 | 0.027066 | 0.55341 | 0.035259 | 1 | 6301.55
2020-12-30 06:00 | 0.48445 | 0.15632 | 0.5412 | 0.075362 | 1 | 6523.47
2020-12-30 06:30 | 0.46689 | 0.32388 | 0.49264 | 0.12717 | 1 | 6851.81
2020-12-30 07:00 | 0.46227 | 0.44936 | 0.42338 | 0.18411 | 1 | 7117.73
2020-12-30 07:30 | 0.4636 | 0.50273 | 0.35066 | 0.23579 | 1 | 7375.87
2020-12-30 08:00 | 0.49566 | 0.53271 | 0.31268 | 0.28015 | 1 | 7627.56
2020-12-30 08:30 | 0.50372 | 0.55842 | 0.28678 | 0.32849 | 1 | 7914.36
2020-12-30 09:00 | 0.50126 | 0.55456 | 0.25236 | 0.37445 | 1 | 8008.4
2020-12-30 09:30 | 0.49976 | 0.55782 | 0.23964 | 0.41769 | 1 | 8221.02
2020-12-30 10:00 | 0.50091 | 0.57733 | 0.21546 | 0.46834 | 1 | 8316.1
2020-12-30 10:30 | 0.47962 | 0.58854 | 0.18886 | 0.52541 | 1 | 8321.69
2020-12-30 11:00 | 0.46789 | 0.59209 | 0.18018 | 0.54482 | 1 | 8348.03
2020-12-30 11:30 | 0.46023 | 0.60413 | 0.16895 | 0.53908 | 1 | 8272.71
2020-12-30 12:00 | 0.45577 | 0.58058 | 0.1627 | 0.51429 | 1 | 8193.05
2020-12-30 12:30 | 0.45903 | 0.58258 | 0.18265 | 0.49062 | 1 | 8150.57
2020-12-30 13:00 | 0.47337 | 0.56236 | 0.20721 | 0.47549 | 1 | 8320.99
2020-12-30 13:30 | 0.47659 | 0.56276 | 0.25487 | 0.44003 | 1 | 8315.27
2020-12-30 14:00 | 0.48938 | 0.56771 | 0.27099 | 0.386 | 1 | 8210.92
2020-12-30 14:30 | 0.51305 | 0.58649 | 0.25838 | 0.34719 | 1 | 8254.94
2020-12-30 15:00 | 0.51518 | 0.54647 | 0.27148 | 0.322 | 1 | 8235.08
2020-12-30 15:30 | 0.54732 | 0.49101 | 0.31717 | 0.27415 | 1 | 8311.24
2020-12-30 16:00 | 0.57576 | 0.4233 | 0.35633 | 0.22439 | 1 | 8303.52
2020-12-30 16:30 | 0.5871 | 0.43335 | 0.40239 | 0.17553 | 1 | 8360.26
2020-12-30 17:00 | 0.58368 | 0.37313 | 0.49045 | 0.13193 | 1 | 8176.18
2020-12-30 17:30 | 0.58311 | 0.3463 | 0.54268 | 0.091998 | 1 | 8033.5
2020-12-30 18:00 | 0.59836 | 0.27548 | 0.52719 | 0.051578 | 1 | 7928.76
2020-12-30 18:30 | 0.62572 | 0.12304 | 0.54453 | 0.018648 | 1 | 7814.48
2020-12-30 19:00 | 0.63115 | 0.03508 | 0.59905 | 0.0036084 | 1 | 7661.45
2020-12-30 19:30 | 0.639 | 0.0015307 | 0.61694 | 0.00027757 | 1 | 7683.75
2020-12-30 20:00 | 0.6353 | 0 | 0.63085 | 0 | 1 | 7659
2020-12-30 20:30 | 0.62344 | 0 | 0.6141 | 0 | 1 | 7532.95
2020-12-30 21:00 | 0.60864 | 0 | 0.60616 | 0 | 1 | 7400.81
2020-12-30 21:30 | 0.6128 | 0 | 0.59611 | 0 | 1 | 7411.36
2020-12-30 22:00 | 0.58561 | 0 | 0.58111 | 0 | 1 | 7288.55
2020-12-30 22:30 | 0.59494 | 0 | 0.56856 | 0 | 1 | 7325.09
2020-12-30 23:00 | 0.56787 | 0 | 0.56208 | 0 | 1 | 7136.4
2020-12-30 23:30 | 0.57868 | 0 | 0.54422 | 0 | 1 | 7057.72
2020-12-31 | 0.56878 | 0 | 0.51286 | 0 | 1 | 6929.66
2020-12-31 00:30 | 0.5461 | 0 | 0.50468 | 0 | 1 | 6765.11
2020-12-31 01:00 | 0.50611 | 0 | 0.50315 | 0 | 1 | 6544.22
2020-12-31 01:30 | 0.45507 | 0 | 0.52109 | 0 | 1 | 6205.7
2020-12-31 02:00 | 0.42428 | 0 | 0.52551 | 0 | 1 | 6021.42
2020-12-31 02:30 | 0.41425 | 0 | 0.5085 | 0 | 1 | 5868.23
2020-12-31 03:00 | 0.40542 | 0 | 0.5422 | 0 | 1 | 5836.14
2020-12-31 03:30 | 0.39757 | 0 | 0.54823 | 0 | 1 | 5776.03
2020-12-31 04:00 | 0.39931 | 0 | 0.53622 | 3.2443e-05 | 1 | 5811.87
2020-12-31 04:30 | 0.41524 | 0 | 0.52991 | 0.0013194 | 1 | 5902.32
2020-12-31 05:00 | 0.42999 | 0.00015479 | 0.5213 | 0.013082 | 1 | 6013.37
2020-12-31 05:30 | 0.44401 | 0.018885 | 0.51466 | 0.042526 | 1 | 6264.85
2020-12-31 06:00 | 0.44229 | 0.082475 | 0.4939 | 0.084998 | 1 | 6451.55
2020-12-31 06:30 | 0.43883 | 0.15972 | 0.48152 | 0.14692 | 1 | 6829.6
2020-12-31 07:00 | 0.42887 | 0.28597 | 0.46436 | 0.21319 | 1 | 7044.39
2020-12-31 07:30 | 0.44721 | 0.37737 | 0.46119 | 0.26797 | 1 | 7379.03
2020-12-31 08:00 | 0.45857 | 0.47572 | 0.42526 | 0.32293 | 1 | 7710.76
2020-12-31 08:30 | 0.46606 | 0.55948 | 0.37788 | 0.38204 | 1 | 7965.47
2020-12-31 09:00 | 0.46056 | 0.55608 | 0.32491 | 0.43221 | 1 | 8022.88
2020-12-31 09:30 | 0.47811 | 0.59342 | 0.29232 | 0.4705 | 1 | 8240.52
2020-12-31 10:00 | 0.48766 | 0.59871 | 0.27013 | 0.49355 | 1 | 8283.37
2020-12-31 10:30 | 0.48492 | 0.62035 | 0.27024 | 0.49857 | 1 | 8373.66
2020-12-31 11:00 | 0.484 | 0.61168 | 0.27445 | 0.48835 | 1 | 8328.68
2020-12-31 11:30 | 0.49298 | 0.61686 | 0.28921 | 0.47731 | 1 | 8328.32
2020-12-31 12:00 | 0.50034 | 0.56686 | 0.25368 | 0.45083 | 1 | 8276.82
2020-12-31 12:30 | 0.50446 | 0.51027 | 0.23012 | 0.43177 | 1 | 8201.1
2020-12-31 13:00 | 0.49501 | 0.50935 | 0.25285 | 0.40496 | 1 | 8110.56
2020-12-31 13:30 | 0.49337 | 0.48064 | 0.28068 | 0.39177 | 1 | 8153.57
2020-12-31 14:00 | 0.48924 | 0.40338 | 0.31434 | 0.39226 | 1 | 8085.69
2020-12-31 14:30 | 0.49788 | 0.33173 | 0.33663 | 0.35329 | 1 | 7977.1
2020-12-31 15:00 | 0.50587 | 0.35765 | 0.39852 | 0.29284 | 1 | 7973.01
2020-12-31 15:30 | 0.52314 | 0.30073 | 0.46462 | 0.24708 | 1 | 7894.04
2020-12-31 16:00 | 0.55568 | 0.3051 | 0.48053 | 0.20267 | 1 | 7968.36
2020-12-31 16:30 | 0.57061 | 0.23552 | 0.46789 | 0.15141 | 1 | 8018.98
2020-12-31 17:00 | 0.57224 | 0.18291 | 0.48972 | 0.10646 | 1 | 7976.85
2020-12-31 17:30 | 0.56452 | 0.15312 | 0.54908 | 0.065914 | 1 | 7755.5
2020-12-31 18:00 | 0.56393 | 0.084436 | 0.63375 | 0.032721 | 1 | 7642.24
2020-12-31 18:30 | 0.55878 | 0.045239 | 0.65582 | 0.011741 | 1 | 7472.74
2020-12-31 19:00 | 0.56966 | 0.010646 | 0.68105 | 0.0022602 | 1 | 7414.52
2020-12-31 19:30 | 0.55404 | 0.00035545 | 0.67627 | 0.00016222 | 1 | 7343.17
2020-12-31 20:00 | 0.5356 | 0 | 0.6661 | 0 | 1 | 7293.57
2020-12-31 20:30 | 0.51505 | 0 | 0.65465 | 0 | 1 | 7159.41
2020-12-31 21:00 | 0.51568 | 0 | 0.64085 | 0 | 1 | 7148.43
2020-12-31 21:30 | 0.50852 | 0 | 0.64624 | 0 | 1 | 7182.3
2020-12-31 22:00 | 0.51311 | 0 | 0.60703 | 0 | 1 | 7230.98
2020-12-31 22:30 | 0.54122 | 0 | 0.57032 | 0 | 1 | 7248.48
2020-12-31 23:00 | 0.54284 | 0 | 0.5516 | 0 | 1 | 7190.65
2020-12-31 23:30 | 0.5531 | 0 | 0.53589 | 0 | 1 | 7167.04
2021-01-01 | 0.52731 | 0 | 0.54108 | 0 | 1 | 7024.97
2021-01-01 00:30 | 0.50911 | 0 | 0.56897 | 0 | 1 | 6817.86
2021-01-01 01:00 | 0.51449 | 0 | 0.60608 | 0 | 1 | 6582.89
2021-01-01 01:30 | 0.46783 | 0 | 0.60021 | 0 | 1 | 6279.68
2021-01-01 02:00 | 0.4376 | 0 | 0.5629 | 0 | 1 | 6031
2021-01-01 02:30 | 0.41877 | 0 | 0.56693 | 0 | 1 | 5844.16
2021-01-01 03:00 | 0.40897 | 0 | 0.58581 | 0 | 1 | 5782.67
2021-01-01 03:30 | 0.40363 | 0 | 0.58242 | 0 | 1 | 5674.4
2021-01-01 04:00 | 0.4035 | 0 | 0.57795 | 1.8024e-05 | 1 | 5689.24
2021-01-01 04:30 | 0.40564 | 0 | 0.56238 | 0.0007462 | 1 | 5727.38
2021-01-01 05:00 | 0.40733 | 0 | 0.5316 | 0.0080171 | 1 | 5755.39
2021-01-01 05:30 | 0.4041 | 0.0074988 | 0.5705 | 0.030115 | 1 | 5854.61
2021-01-01 06:00 | 0.39856 | 0.054504 | 0.57781 | 0.062947 | 1 | 5961.84
2021-01-01 06:30 | 0.39781 | 0.10373 | 0.57518 | 0.1134 | 1 | 6127.23
2021-01-01 07:00 | 0.39723 | 0.13131 | 0.56759 | 0.16538 | 1 | 6327.52
2021-01-01 07:30 | 0.3979 | 0.14759 | 0.54269 | 0.20366 | 1 | 6530.94
2021-01-01 08:00 | 0.39793 | 0.22496 | 0.51446 | 0.2464 | 1 | 6794.39
2021-01-01 08:30 | 0.40036 | 0.24223 | 0.52435 | 0.2866 | 1 | 7019.11
2021-01-01 09:00 | 0.40138 | 0.25827 | 0.52364 | 0.32079 | 1 | 7191.69
2021-01-01 09:30 | 0.40354 | 0.30386 | 0.4923 | 0.36482 | 1 | 7381.96
2021-01-01 10:00 | 0.39804 | 0.33117 | 0.43637 | 0.38993 | 1 | 7429.07
2021-01-01 10:30 | 0.40053 | 0.36538 | 0.37383 | 0.39471 | 1 | 7527.11
2021-01-01 11:00 | 0.40011 | 0.40711 | 0.33091 | 0.40175 | 1 | 7586.61
2021-01-01 11:30 | 0.40301 | 0.41263 | 0.26767 | 0.38558 | 1 | 7602.81
2021-01-01 12:00 | 0.40455 | 0.36861 | 0.26374 | 0.36646 | 1 | 7583.05
2021-01-01 12:30 | 0.40657 | 0.33412 | 0.26065 | 0.34479 | 1 | 7501.51
2021-01-01 13:00 | 0.41036 | 0.37752 | 0.27274 | 0.32578 | 1 | 7467.59
2021-01-01 13:30 | 0.40684 | 0.37441 | 0.29129 | 0.315 | 1 | 7383.48
2021-01-01 14:00 | 0.40739 | 0.42474 | 0.31158 | 0.28738 | 1 | 7300.56
2021-01-01 14:30 | 0.4127 | 0.47982 | 0.33655 | 0.26661 | 1 | 7294.4
2021-01-01 15:00 | 0.41187 | 0.40794 | 0.37378 | 0.2459 | 1 | 7268.19
2021-01-01 15:30 | 0.41552 | 0.37045 | 0.37765 | 0.2087 | 1 | 7235.27
2021-01-01 16:00 | 0.43505 | 0.29368 | 0.3852 | 0.17139 | 1 | 7335.09
2021-01-01 16:30 | 0.45836 | 0.25836 | 0.39636 | 0.1331 | 1 | 7394.14
2021-01-01 17:00 | 0.49704 | 0.2069 | 0.42462 | 0.096544 | 1 | 7402.85
2021-01-01 17:30 | 0.52704 | 0.16003 | 0.47017 | 0.064526 | 1 | 7398.36
2021-01-01 18:00 | 0.5479 | 0.10311 | 0.51247 | 0.037825 | 1 | 7347.46
2021-01-01 18:30 | 0.55727 | 0.051947 | 0.58089 | 0.013933 | 1 | 7242.18
2021-01-01 19:00 | 0.56913 | 0.010841 | 0.56606 | 0.0024044 | 1 | 7193.69
2021-01-01 19:30 | 0.58215 | 0 | 0.48845 | 0.00014419 | 1 | 7266.77
2021-01-01 20:00 | 0.57496 | 0 | 0.4932 | 0 | 1 | 7188.18
2021-01-01 20:30 | 0.55474 | 0 | 0.50955 | 0 | 1 | 7108.78
2021-01-01 21:00 | 0.53667 | 0 | 0.56305 | 0 | 1 | 7008.45
2021-01-01 21:30 | 0.53948 | 0 | 0.55948 | 0 | 1 | 7052.3
2021-01-01 22:00 | 0.52794 | 0 | 0.60764 | 0 | 1 | 7027.43
2021-01-01 22:30 | 0.52237 | 0 | 0.65374 | 0 | 1 | 7003.14
2021-01-01 23:00 | 0.51367 | 0 | 0.65399 | 0 | 1 | 6938.79
2021-01-01 23:30 | 0.49957 | 0 | 0.65423 | 0 | 1 | 6821.16
2021-01-02 | 0.47929 | 0 | 0.65102 | 0 | 1 | 6675.88
2021-01-02 00:30 | 0.47198 | 0 | 0.63323 | 0 | 1 | 6477.3
2021-01-02 01:00 | 0.46529 | 0 | 0.60319 | 0 | 1 | 6253.61
2021-01-02 01:30 | 0.44527 | 0 | 0.58503 | 0 | 1 | 5997.1
2021-01-02 02:00 | 0.43294 | 0 | 0.58425 | 0 | 1 | 5826.82
2021-01-02 02:30 | 0.42336 | 0 | 0.58394 | 0 | 1 | 5714.41
2021-01-02 03:00 | 0.42106 | 0 | 0.57993 | 0 | 1 | 5605.26
2021-01-02 03:30 | 0.42877 | 0 | 0.595 | 0 | 1 | 5591.79
2021-01-02 04:00 | 0.42925 | 0 | 0.56218 | 7.2096e-06 | 1 | 5629.44
2021-01-02 04:30 | 0.42551 | 0 | 0.53595 | 0.00065608 | 1 | 5664.04
2021-01-02 05:00 | 0.42769 | 0.00019492 | 0.50534 | 0.0079811 | 1 | 5747.25
2021-01-02 05:30 | 0.43852 | 0.015502 | 0.48413 | 0.029657 | 1 | 5874.33
2021-01-02 06:00 | 0.45675 | 0.058941 | 0.47187 | 0.058913 | 1 | 6051.35
2021-01-02 06:30 | 0.44648 | 0.1468 | 0.41385 | 0.094461 | 1 | 6323.47
2021-01-02 07:00 | 0.44743 | 0.19834 | 0.39168 | 0.14348 | 1 | 6596.16
2021-01-02 07:30 | 0.45181 | 0.23058 | 0.3542 | 0.19975 | 1 | 6926.12
2021-01-02 08:00 | 0.45573 | 0.26816 | 0.33304 | 0.24146 | 1 | 7208.77
2021-01-02 08:30 | 0.46287 | 0.32152 | 0.25968 | 0.28538 | 1 | 7434.86
2021-01-02 09:00 | 0.46601 | 0.32859 | 0.19371 | 0.32839 | 1 | 7530.58
2021-01-02 09:30 | 0.46642 | 0.34216 | 0.15511 | 0.35549 | 1 | 7603.75
2021-01-02 10:00 | 0.46355 | 0.32002 | 0.12971 | 0.38865 | 1 | 7675.07
2021-01-02 10:30 | 0.46067 | 0.3553 | 0.11928 | 0.43168 | 1 | 7767.11
2021-01-02 11:00 | 0.45967 | 0.35689 | 0.13163 | 0.43544 | 1 | 7698.27
2021-01-02 11:30 | 0.4581 | 0.36924 | 0.15092 | 0.43167 | 1 | 7708.85
2021-01-02 12:00 | 0.45909 | 0.33528 | 0.17618 | 0.43162 | 1 | 7715.13
2021-01-02 12:30 | 0.46561 | 0.33041 | 0.18701 | 0.41612 | 1 | 7630.59
2021-01-02 13:00 | 0.46625 | 0.33158 | 0.20741 | 0.38631 | 1 | 7581.86
2021-01-02 13:30 | 0.4633 | 0.36096 | 0.30148 | 0.35218 | 1 | 7560.74
2021-01-02 14:00 | 0.46257 | 0.40814 | 0.35656 | 0.33066 | 1 | 7652.3
2021-01-02 14:30 | 0.47376 | 0.38408 | 0.36288 | 0.29366 | 1 | 7618.58
2021-01-02 15:00 | 0.48032 | 0.34012 | 0.43423 | 0.25182 | 1 | 7584.16
2021-01-02 15:30 | 0.48636 | 0.2927 | 0.43606 | 0.20535 | 1 | 7508.45
2021-01-02 16:00 | 0.51123 | 0.27909 | 0.40643 | 0.16274 | 1 | 7627.15
2021-01-02 16:30 | 0.52208 | 0.24635 | 0.44609 | 0.13303 | 1 | 7647.59
2021-01-02 17:00 | 0.54441 | 0.18612 | 0.44035 | 0.098112 | 1 | 7694.06
2021-01-02 17:30 | 0.5437 | 0.14625 | 0.46914 | 0.076426 | 1 | 7619.19